## Sheet1
Rev | Disc. | Unit | SWGR/MCC No. | Bus | SWGR/MCC No. & Bus | Equipment Tag No. | EQUIPMENT Description | Type of Service | Load Type | Voltage | Starter Type | Load Duty | Absorbed Power | Rated Power | Full Load Current | DUTY | Efficiency (%) | Power Factor | UTILIZATION (UF) | Consumed Load | 세로 막대형1 | 세로 막대형2 | 세로 막대형3 | 세로 막대형4 | 세로 막대형5 | Variation from FEED | Variation from FEED Detail | Remarks | Location (Building) | History | 세로 막대형6
[10 empty] | [KV] |  |  | (kW) | (kW) |  | Load Factor | [C] | [D] | (%) | [6 empty] | (Added/Deleted/Increased/
[8 empty] | N-Normal, | [5 empty] | [B] |  | [A/B] |  |  | [E] | [6 empty] | Decreased/No Change)
[8 empty] | Em-Emergency, |  |  |  |  | [A]
SA-UPS Power
kW=(B/C)*E, kVAr=(B/C)*TAN(ACOS(D))*(F)
[20 empty] | Continuous [F] |  | Intermittent [G] |  | Standby [H]
[20 empty] | [kW] | [kVAr] | [kW] | [kVAr] | [kW] | [kVAr]
C1 | MR | 3 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1003 | Export Compressor _ Main Motor | N | VSD-HV | 11 | VVVF | C | 10237 | 11000 | 613.6149 | 0.93064 | 97 | 0.97 | 100 | 10553.6082 | 2644.9835 | 0 | 0 | 0 | 0 | Increased | 8000KW -> 11000KW |  |  | 20251202 IOM-ME(MR)-0003 수정
[6 empty] | Main Motor | [23 empty] | 20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260128 IOM-ME(MR)-0010 수정
C1 | MR | 3 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-KA-31-2003 | Export Compressor _ Main Motor | N | VSD-HV | 11 | VVVF | C | 10237 | 11000 | 613.6149 | 0.93064 | 97 | 0.97 | 100 | 10553.6082 | 2644.9835 | 0 | 0 | 0 | 0 | Increased | 8000KW -> 11000KW |  |  | 20251202 IOM-ME(MR)-0003 수정
[6 empty] | Main Motor | [23 empty] | 20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260128 IOM-ME(MR)-0010 수정
| EL | 5 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0001A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11 |  | C | [6 empty] | 100 | 352.315 | 115.8003 | 198.1388 | 8.6606 | 101.1244 | 43.8308 |  |  |  | MAIN SUBSTATION | FEED
D3 | EL | 5 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0001B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgeard B | N | F | 11 |  | C | [6 empty] | 100 | 1718.9095 | 798.0793 | 322.1382 | 44.4608 | 49.4269 | 31.0742 |  |  |  | MAIN SUBSTATION | FEED
| EL | 5 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0003A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11 |  | C | [6 empty] | 100 | 2073.7363 | 1061.3929 | 79.2572 | 28.3584 | 9.386 | 5.801 |  |  |  | MAIN SUBSTATION | FEED
| EL | 5 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0003B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgear B | N | F | 11 |  | C | [6 empty] | 100 | 463.4922 | 184.4036 | 70.9837 | 30.082 | 221.2006 | 90.3108 |  |  |  | MAIN SUBSTATION | FEED
| EL | 5 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0002A | 11/0.42kV Transformer Feeder A for 400V Normal Switchgear A | N | F | 11 |  | C | [6 empty] | 100 | 938.5494 | 586.87 | 49.509 | 32.7801 | 72.1303 | 8.1281 |  |  |  | MAIN SUBSTATION | FEED
| EL | 5 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0002B | 11/0.42kV Transformer Feeder B for 400V Normal Switchgear B | N | F | 11 |  | C | [6 empty] | 100 | 320.5748 | 200.2969 | 37.5451 | 24.1478 | 43.2005 | 28.3333 |  |  |  | MAIN SUBSTATION | FEED
D4 | MR | 2 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-A-20-0002A -Main Motor | Condensate Recycle Booster Pump A | N | M-HV | 11 |  | I | 539 | 720 | 46.799 | 0.74861 | 95 | 0.85 | 30 | 0 | 0 | 170.2105 | 105.487 | 0 | 0 | No Change Increased | 600KW -> 720KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 2 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-A-20-0002B -Main Motor | Condensate Recycle Booster Pump B | N | M-HV | 11 |  | S | 539 | 720 | 46.799 | 0.74861 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 56.7368 | 35.1623 | No Change Increased | 600KW -> 720KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260317 IOM-ME(MR)-0016 Rating 수정
| MR | 3 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1001/1002-Main Motor | Main Motor for Flash Gas Compressor | N | M-HV | 11 |  | C | 1044 | 1500 | 97.4979 | 0.696 | 95 | 0.85 | 100 | 1098.9474 | 681.0664 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
D3 | MR | 5 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-PA-01-0002 Panel(Main Motor Power) | Electric Firewater Pump Motor | N | M-HV | 11 |  | I | 311 | 400 | 25.9994 | 0.7775 | 95 | 0.85 | 30 | 0 | 0 | 98.2105 | 60.8654 | 0 | 0 | Decreased | 560KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 (VVVF->SS) 수정
20260130 VE SS 삭제, Normal 변경
20260225 IOM-ME(MR)-0014 Description / Rating 수정
D4 | MS | 4 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-UZ-43-0002 | 11/0.72kV Transformer for MEG Regeneration Package - Electric Reboiler (2 x 100%) | N | F | 11 |  | C | 3100 | 3100 | 171.2714 | 1 | 95 | 1 | 100 | 3263.1579 | 0 | 0 | 0 | 0 | 0 | Increased | 3000KW -> 3100KW | Dedicated TR (4MVA) |  | 20250105 IOM-ME(MS)-0005 Description 수정
20260129 IOM-ME(MS)-0011 Dedicated TR 추가
20260225 IOM-ME(MS)-0026 Rating 수정
20260317 IOM-ME(MS)-0032 Description 오타 수정
D4 | MS | 4 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-UZ-43-0002-SP | 11/0.72kV Transformer for MEG Regeneration Package - Electric Reboiler (2 x 100%) - Spare | N | F | 11 |  | S | 3100 | 3100 | 171.2714 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 326.3158 | 0 | Added |  | Dedicated TR (4MVA) |  | Spare for MEG PKG Electric Heater
20260225 IOM-ME(MS)-0026 Rating 수정
20260317 IOM-ME(MS)-0032 Description 오타 수정
D3 | MS | 3 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-HE-35-0001-TR | 11/0.72kV Transformer for Start up Gas Heater | N | F | 11 |  | I | 530 | 750 | 41.4366 | 0.70667 | 95 | 1 | 30 | 0 | 0 | 167.3684 | 0 | 0 | 0 | No Change |  | Dedicated TR (750kVA) |  | 20260303 추가 (TQ-720)
D | FF | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-DM-01-0004A | Electric Fire Fighting Foam Skid Pump Motor A | Em | M-B1 | 0.69 |  | I | 78 | 90 | 94.251 | 0.86667 | 94 | 0.85 | 30 | 0 | 0 | 24.8936 | 15.4277 | 0 | 0 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 기준 Deleted (FEED에만 있음)
20260206 복구함 (by FF)
20260306 consumed load 수식 복구
D | FF | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-DM-01-0004B | Electric Fire Fighting Foam Skid Pump Motor B | Em | M-B1 | 0.69 |  | S | 78 | 90 | 94.251 | 0.86667 | 94 | 0.85 | 10 | 0 | 0 | 0 | 0 | 8.2979 | 5.1426 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 기준 Deleted (FEED에만 있음)
20260206 복구함 (by FF)
20260306 consumed load 수식 복구
D | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HF-05-0001A | Emergency Generator auxiliaries MCC supply A | Em | PDB | 0.69 |  | C | 13.5 | 65 | 63.986 | 0.20769 | 100 | 0.85 | 100 | 13.5 | 8.3665 | 0 | 0 | 0 | 0 | Increased | 50KW -> 65KW |  | MAIN SUBSTATION | FEED
20251216 Load Type 수정
D | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HF-05-0001B | Emergency Generator auxiliaries MCC supply B | Em | PDB | 0.69 |  | S | 13.5 | 65 | 63.986 | 0.20769 | 100 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Increased | 50KW -> 65KW |  | MAIN SUBSTATION | FEED
20251216 Load Type 수정
| EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0001A | 110V DC UPS A for Main Substation | Em | U | 0.69 |  | S | 5 | 5 | 4.922 | 1 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.5 | 0.30987 | No Change |  |  | MAIN SUBSTATION | FEED
| EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0001B | 110V DC UPS B for Main Substation | Em | U | 0.69 |  | C | 5 | 5 | 4.922 | 1 | 100 | 0.85 | 100 | 5 | 3.0987 | 0 | 0 | 0 | 0 | No Change |  |  | MAIN SUBSTATION | FEED
D4 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0002A | 230V AC UPS A in Main Substation for Telecomms | Em | U | 0.69 |  | S | 5.35 | 10 | 9.844 | 0.535 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.535 | 0.33156 | No Change |  |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0002B | 230V AC UPS B in Main Substation for Telecomms | Em | U | 0.69 |  | C | 5.35 | 10 | 9.844 | 0.535 | 100 | 0.85 | 80 | 4.28 | 2.6525 | 0 | 0 | 0 | 0 | No Change |  |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0002 | 230V UPS Feeder Maintenance Bypass for Main Substation Telecomms | Em | U | 0.69 |  | S | 5.35 | 10 | 9.844 | 0.535 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.535 | 0.33156 | No Change |  |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0003A | 230V AC UPS A in Process - ITR for Telecomms | Em | U | 0.69 |  | S | 15.36 | 20 | 19.688 | 0.768 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.536 | 0.95193 | Increased | 10kVA -> 25kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0003B | 230V AC UPS B in Process - ITR for Telecomms | Em | U | 0.69 |  | C | 15.36 | 20 | 19.688 | 0.768 | 100 | 0.85 | 80 | 12.288 | 7.6154 | 0 | 0 | 0 | 0 | Increased | 10kVA -> 25kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0003 | 230V UPS Feeder Maintenance Bypass for Process - ITR Telecomms | Em | U | 0.69 |  | S | 15.36 | 20 | 19.688 | 0.768 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.536 | 0.95193 | Increased | 10kVA -> 25kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0004A | 230V AC UPS A in Process - ITR for Instruments | Em | U | 0.69 |  | S | 74.38 | 90 | 88.5959 | 0.82644 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 7.438 | 4.6097 | Increased | 50kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0004B | 230V AC UPS B in Process - ITR for Instruments | Em | U | 0.69 |  | C | 74.38 | 90 | 88.5959 | 0.82644 | 100 | 0.85 | 100 | 74.38 | 46.0966 | 0 | 0 | 0 | 0 | Increased | 50kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0004 | 230V UPS Feeder Maintenance Bypass for Process - ITR Instruments | Em | U | 0.69 |  | S | 74.38 | 90 | 88.5959 | 0.82644 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 7.438 | 4.6097 | Increased | 50kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0005A | 230V AC UPS A in Utility - ITR for Telecomms | Em | U | 0.69 |  | S | 8 | 10 | 9.844 | 0.8 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.8 | 0.4958 | Increased | 10kVA -> 15kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0005B | 230V AC UPS B in Utility - ITR for Telecomms | Em | U | 0.69 |  | C | 8 | 10 | 9.844 | 0.8 | 100 | 0.85 | 80 | 6.4 | 3.9664 | 0 | 0 | 0 | 0 | Increased | 10kVA -> 15kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0005 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Telecomms | Em | U | 0.69 |  | S | 8 | 10 | 9.844 | 0.8 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.8 | 0.4958 | Increased | 10kVA -> 15kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0006A | 230V AC UPS A in Utility - ITR for Instruments | Em | U | 0.69 |  | S | 64.2 | 80 | 78.752 | 0.8025 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 6.42 | 3.9788 | Increased | 50kVA -> 80kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0006B | 230V AC UPS B in Utility - ITR for Instruments | Em | U | 0.69 |  | C | 64.2 | 80 | 78.752 | 0.8025 | 100 | 0.85 | 100 | 64.2 | 39.7876 | 0 | 0 | 0 | 0 | Increased | 50kVA -> 80kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0006 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Instruments | Em | U | 0.69 |  | S | 64.2 | 80 | 78.752 | 0.8025 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 6.42 | 3.9788 | Increased | 50kVA -> 80kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0007A | 230V AC UPS A in Control Building for Telecomms | Em | U | 0.69 |  | S | 51.9 | 70 | 68.908 | 0.74143 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 5.19 | 3.2165 | Increased | 60kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0007B | 230V AC UPS B in Control Building for Telecomms | Em | U | 0.69 |  | C | 51.9 | 70 | 68.908 | 0.74143 | 100 | 0.85 | 80 | 41.52 | 25.7318 | 0 | 0 | 0 | 0 | Increased | 60kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0007 | 230V UPS Feeder Maintenance Bypass for Control Building Telecomms | Em | U | 0.69 |  | S | 51.9 | 70 | 68.908 | 0.74143 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 5.19 | 3.2165 | Increased | 60kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0008A | 230V AC UPS A in Control Building for Instruments | Em | U | 0.69 |  | S | 94.79 | 130 | 127.9719 | 0.72915 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 9.479 | 5.8746 | Increased | 70kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0008B | 230V AC UPS B in Control Building for Instruments | Em | U | 0.69 |  | C | 94.79 | 130 | 127.9719 | 0.72915 | 100 | 0.85 | 100 | 94.79 | 58.7456 | 0 | 0 | 0 | 0 | Increased | 70kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0008 | 230V UPS Feeder Maintenance Bypass for Control Building Instruments | Em | U | 0.69 |  | S | 94.79 | 130 | 127.9719 | 0.72915 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 9.479 | 5.8746 | Increased | 70kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0010A | 230V AC UPS A in Workshop for Telecoms | Em | U | 0.69 |  | S | 9.98 | 15 | 14.766 | 0.66533 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.998 | 0.6185 | Increased | 10kVA -> 20kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0010B | 230V AC UPS B in Workshop for Telecoms | Em | U | 0.69 |  | C | 9.98 | 15 | 14.766 | 0.66533 | 100 | 0.85 | 80 | 7.984 | 4.948 | 0 | 0 | 0 | 0 | Increased | 10kVA -> 20kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0010 | 230V UPS Feeder Maintenance Bypass for Workshop Telecoms | Em | U | 0.69 |  | S | 9.98 | 15 | 14.766 | 0.66533 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.998 | 0.6185 | Increased | 10kVA -> 20kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0011A | 230V AC UPS A in Adminstration Building for Telecoms | Em | U | 0.69 |  | S | 34.98 | 50 | 49.22 | 0.6996 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 3.498 | 2.1679 | Increased | 40kVA -> 60kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0011B | 230V AC UPS B in Adminstration Building for Telecoms | Em | U | 0.69 |  | C | 34.98 | 50 | 49.22 | 0.6996 | 100 | 0.85 | 80 | 27.984 | 17.3429 | 0 | 0 | 0 | 0 | Increased | 40kVA -> 60kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 5 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0011 | 230V UPS Feeder Maintenance Bypass for Adminstration Building Telecoms | Em | U | 0.69 |  | S | 34.98 | 50 | 49.22 | 0.6996 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 3.498 | 2.1679 | Increased | 40kVA -> 60kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0003A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Control Building Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 180.99 | 59.4885 | 0 | 0 | 0 | 0 |  |  |  | CONTROL BUILDING | FEED
20251216 Description / Load Type 수정
D | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0003B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Control Building Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 96.546 | 31.7331 | 16.8156 | 5.527 | 27.7203 | 9.1112 |  |  |  | CONTROL BUILDING | FEED
20251216 Description / Load Type 수정
D | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0005A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Substation Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 79.39 | 26.0942 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED
20251216 Description / Load Type 수정
D | EL | 5 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0005B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Substation Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 161.327 | 53.0256 | 2.1978 | 0.72238 | 12.0129 | 3.9484 |  |  |  | MAIN SUBSTATION | FEED
20251216 Description / Load Type 수정
D | EL | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0006A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR East-Utilities Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 84.16 | 27.6621 | 0 | 0 | 0 | 0 |  |  |  | ITR EAST | FEED
20251216 Description / Load Type 수정
D | EL | 4 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0006B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR East-Utilities Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 50.711 | 16.6679 | 4.2471 | 1.396 | 13.4871 | 4.433 |  |  |  | ITR EAST | FEED
20251216 Description / Load Type 수정
D | EL | 3 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0007A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR West-Process Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 71.37 | 23.4582 | 0 | 0 | 0 | 0 |  |  |  | ITR WEST | FEED
20251216 Description / Load Type 수정
D | EL | 3 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0007B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR West-Process Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 43.731 | 14.3737 | 3.0888 | 1.0152 | 11.5101 | 3.7832 |  |  |  | ITR WEST | FEED
20251216 Description / Load Type 수정
C1 | MS | 1 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-HE-36-0002A | HP Flare KO Drum Heater A | N | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음)
20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 1 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0002B | HP Flare KO Drum Heater B | Em | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음)
20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 1 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0003 | LP Flare KO Drum Heater | Em | H2 | 0.69 |  | I | 266 | 320 | 281.8491 | 0.83125 | 95 | 1 | 30 | 0 | 0 | 84 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음)
20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C5 | EL | 7 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0001 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Gate house - Indoor (70-IG-62-0001) | Em | L | 0.69 |  | C | 3.55 | 5 | 4.922 | 0.71 | 100 | 0.85 | 100 | 3.55 | 2.2001 | 0 | 0 | 0 | 0 |  |  |  | MAIN GATE HOUSE | 20251216 FEED EQ LIST Added
C5 | EL | 7 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0002 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Access control building Security HUT 02 - Indoor (70-IG-62-0002) | Em | L | 0.69 |  | C | 3.55 | 5 | 4.922 | 0.71 | 100 | 0.85 | 100 | 3.55 | 2.2001 | 0 | 0 | 0 | 0 |  |  |  | SECURITY HUT 02 | FEED
C5 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0003 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Control Building - Indoor (70-IG-62-0003) | Em | L | 0.69 |  | C | 13 | 15 | 14.766 | 0.86667 | 100 | 0.85 | 100 | 13 | 8.0567 | 0 | 0 | 0 | 0 |  |  |  | CONTROL BUILDING | FEED
C5 | EL | 6 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0006 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Workshop & Warehouse - Indoor (70-IG-62-0006) | Em | L | 0.69 |  | C | 11.4 | 15 | 14.766 | 0.76 | 100 | 0.85 | 100 | 11.4 | 7.0651 | 0 | 0 | 0 | 0 |  |  |  | WORKSHOP & WAREHOUSE | FEED
C5 | EL | 6 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0007 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Adminstration Building - Indoor (70-IG-62-0007) | Em | L | 0.69 |  | C | 24 | 30 | 29.532 | 0.8 | 100 | 0.85 | 100 | 24 | 14.8739 | 0 | 0 | 0 | 0 |  |  |  | ADMINISTRATION BUILDING | FEED
C5 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0009 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Substation - Indoor A (70-IG-62-0009) | Em | L | 0.69 |  | C | 15 | 15 | 14.766 | 1 | 100 | 0.85 | 100 | 15 | 9.2962 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED
C5 | EL | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0011 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor A (70-IG-62-0011) | Em | L | 0.69 |  | C | 14.1 | 15 | 14.766 | 0.94 | 100 | 0.85 | 100 | 14.1 | 8.7384 | 0 | 0 | 0 | 0 |  |  |  | ITR EAST | FEED
C3 | EL | 0 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0013 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0013) | Em | L | 0.69 |  | C | 27 | 32 | 31.5008 | 0.84375 | 100 | 0.85 | 100 | 27 | 16.7331 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 0 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0014 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0014) | Em | L | 0.69 |  | C | 27 | 32 | 31.5008 | 0.84375 | 100 | 0.85 | 100 | 27 | 16.7331 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 0 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0015 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0015) | Em | L | 0.69 |  | C | 27 | 32 | 31.5008 | 0.84375 | 100 | 0.85 | 100 | 27 | 16.7331 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C5 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0051 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Substation - Indoor B (70-IG-62-0051) | Em | F | 0.69 |  | C | 22.5 | 32 | 31.5008 | 0.70312 | 100 | 0.85 | 100 | 22.5 | 13.9442 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED
C5 | EL | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0052 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor B (70-IG-62-0052) | Em | F | 0.69 |  | C | 19.5 | 32 | 31.5008 | 0.60938 | 100 | 0.85 | 100 | 19.5 | 12.085 | 0 | 0 | 0 | 0 |  |  |  | ITR EAST | FEED
C5 | EL | 5 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-65-0080 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency Heat Tracing DB - Main Substation - Indoor (70-IG-65-0080) | Em | PDB | 0.69 |  | C | 60 | 85 | 71.1229 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED
20251216 Load Type 수정
C3 | EL | 3 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0094 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP Main Distribution Board (70-IG-62-0094) | Em | L | 0.69 |  | C | [6 empty] | 100 | 250 | 43.3821 | 34.77 | 24.2696 | 0 | 0 |  |  |  | ITR West | 20260203 MDB 추가
C1 | MR | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Main Motor | Main Motor for Air Compressor Package | Em | M-E1 (SS) | 0.69 | SS | C | 380 | 400 | 414.484 | 0.95 | 95 | 0.85 | 100 | 400 | 247.8977 | 0 | 0 | 0 | 0 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400)
20250105 IOM-ME(MR)-0007 수정 (400->690)
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260109 Bus 수정
20260128 IOM-ME(MR)-0010 Rating 수정
D3 | MR | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Cooling Fan Motor 1 | Cooling Fan Motor 1 for Air Compressor Package | Em | M-B1 | 0.69 |  | C | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 100 | 30.0668 | 20.9868 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260105 IOM-ME(MR)-0007 Tag, Rating 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Cooling Fan Motor 2 | Cooling Fan Motor 2 for Air Compressor Package | Em | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260105 IOM-ME(MR)-0007 Tag, Rating 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260128 IOM-ME(MR)-0010 duty 수정
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Container Fan Motor 1 | Container Fan Motor 1 for Air Compressor Package | Em | M-A1 | 0.69 |  | C | 2.7 | 3 | 3.409 | 0.9 | 89.8 | 0.82 | 100 | 3.0067 | 2.0987 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260225 IOM-ME(MR)-0014 Description 수정
B4 | MR | 1 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0001A Motor | Motor for HP Flare KO Drum Pump | Em | M-B1 | 0.69 |  | I | 14.7 | 18.5 | 20.6088 | 0.79459 | 91.6 | 0.82 | 30 | 0 | 0 | 4.8144 | 3.3605 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400)
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260109 Bus 수정
B4 | MR | 1 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0001B Motor | Motor for HP Flare KO Drum Pump | Em | M-A1 | 0.69 |  | S | 14.7 | 18.5 | 20.6088 | 0.79459 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.6048 | 1.1202 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400)
20251216 Load Type 수정
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260109 Bus 수정
B4 | MR | 1 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0004A Motor | Motor for LP Flare KO Drum Pump | Em | M-A1 | 0.69 |  | I | 5.4 | 11 | 13.2854 | 0.49091 | 86.6 | 0.8 | 30 | 0 | 0 | 1.8707 | 1.403 | 0 | 0 | Increased | 7.5KW -> 11KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400)
20251216 Load Type 수정
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260109 Bus 수정
B4 | MR | 1 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-PA-36-0004B Motor | Motor for LP Flare KO Drum Pump | N | M-A1 | 0.69 |  | S | 5.4 | 11 | 13.2854 | 0.49091 | 86.6 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.62356 | 0.46767 | Increased | 7.5KW -> 11KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400)
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
C1 | MS | 1 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-HE-36-0005A | HP Flare KO Drum B Heater A | N | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음)
20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 1 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0005B | HP Flare KO Drum B Heater B | Em | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음)
20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 1 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-HE-28-0001 | Closed Drains Drum Heater | N | H2 | 0.69 |  | I | 68 | 84 | 73.9854 | 0.80952 | 95 | 1 | 30 | 0 | 0 | 21.4737 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음)
20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
D1 | MR | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001B-Main Motor | Main Motor for Air Compressor Package | N | M-E1 (SS) | 0.69 | SS | C | 380 | 400 | 414.484 | 0.95 | 95 | 0.85 | 100 | 400 | 247.8977 | 0 | 0 | 0 | 0 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400)
20250105 IOM-ME(MR)-0007 수정 (400->690)
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260128 IOM-ME(MR)-0010 Rating 수정
D1 | MR | 4 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UA-07-0001C-Main Motor | Main Motor for Air Compressor Package | N | M-E1 (SS) | 0.69 | SS | S | 380 | 400 | 414.484 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 40 | 24.7898 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400)
20250105 IOM-ME(MR)-0007 수정 (400->690)
20260128 IOM-ME(MR)-0010 Rating 수정
D3 | MR | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001B-Cooling Fan Motor 1 | Cooling Fan Motor 1 for Air Compressor Package | N | M-B1 | 0.69 |  | C | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 100 | 30.0668 | 20.9868 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260105 IOM-ME(MR)-0007 Tag, Rating 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UA-07-0001B-Cooling Fan Motor 2 | Cooling Fan Motor 2 for Air Compressor Package | N | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260105 IOM-ME(MR)-0007 Tag, Rating 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260128 IOM-ME(MR)-0010 duty 수정
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001B-Container Fan Motor 1 | Container Fan Motor 1 for Air Compressor Package | N | M-A1 | 0.69 |  | C | 2.7 | 3 | 3.409 | 0.9 | 89.8 | 0.82 | 100 | 3.0067 | 2.0987 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001C-Cooling Fan Motor 1 | Cooling Fan Motor 1 for Air Compressor Package | N | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260105 IOM-ME(MR)-0007 Tag, Rating 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260128 IOM-ME(MR)-0010 duty 수정
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UA-07-0001C-Cooling Fan Motor 2 | Cooling Fan Motor 2 for Air Compressor Package | N | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260105 IOM-ME(MR)-0007 Tag, Rating 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260128 IOM-ME(MR)-0010 duty 수정
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001C-Container Fan Motor 1 | Container Fan Motor 1 for Air Compressor Package | N | M-A1 | 0.69 |  | S | 2.7 | 3 | 3.409 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.30067 | 0.20987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
20260128 IOM-ME(MR)-0010 duty 수정
20260225 IOM-ME(MR)-0014 Description 수정
D3 | EL | 6 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-09-0004A | 0.4/0.42kV Dry type Transformer for 400/230 HVAC MCC for Adminstration Building Incomer A | N | HVAC MCC | 0.69 |  | C |  |  | #DIV/0! |  |  |  | 100 | 193.925 | 63.7401 | 4.752 | 1.5619 | 1.9796 | 0.65066 |  |  | Moved from 70-IK-61-0003 | ADMINISTRATION BUILDING | FEED
20251216 Description / Load Type 수정
D2 | EL | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-62-0093 | 0.69/0.42kV Dry type Transformer for 400/230V Normal L & SP Main Distribution Board (70-IG-62-0093) | N | L | 0.69 |  | C |  |  | #DIV/0! |  |  |  | 100 | 167.3684 | 51.5366 | 0 | 0 | 59.7267 | 0 |  |  | Moved from 70-IK-61-0002 | ITR West | 20260203 MDB 추가
D5 | EL | 6 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-IV-09-0002A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Workshop & Warehouse Incomer A | N | HVAC MCC | 0.69 |  | C | [6 empty] | 100 | 399.041 | 131.1584 | 59.2893 | 19.4875 | 1.6146 | 0.53069 |  |  | Moved to 70-IK-61-0002 | WORKSHOP & WAREHOUSE | FEED
20251216 Description / Load Type 수정
D5 | EL | 7 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-IV-09-0010A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Gate House Incomer A | N | HVAC MCC | 0.69 |  | C | 0 | 0 |  |  |  |  | 100 | 38.489 | 12.6507 | 6.7743 | 2.2266 | 0.0666 | 0.02189 |  |  | Moved to 70-IK-61-0002 | MAIN GATE HOUSE | FEED
20251216 Description / Load Type 수정
D5 | EL | 7 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-09-0011A | 0.40/0.42kV Dry type Transformer for 400/230 HVAC MCC for HUT 02 Incomer A | N | HVAC MCC | 0.69 |  | C | 0 | 0 |  |  |  |  | 100 | 7.884 | 2.5913 | 0.81 | 0.26623 | 0 | 0 |  |  | Moved to 70-IK-61-0002 | SECURITY HUT 02 | FEED
20251216 Description / Load Type 수정
C1 | MR | 1 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-DM-36-0003A | Main Motor for Liquid Ring Compressor (70-KG-36-0003A) | N | VSD-G2 | 0.69 | VVVF | C | 320 | 355 | 367.8545 | 0.90141 | 95 | 0.85 | 100 | 336.8421 | 208.756 | 0 | 0 | 0 | 0 | Decreased | 400KW -> 355KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 (VVVF->SS) 수정
20260128 IOM-ME(MR)-0010 (SS->VVVF) 수정
B2 | MR | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-PA-25-0001A Motor | Motor for Condensate Export Pump | N | M-E1 | 0.69 |  | C | 221 | 250 | 258.5083 | 0.884 | 95.2 | 0.85 | 100 | 232.1429 | 143.8692 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating 수정
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
B4 | MR | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-PA-25-0001B Motor | Motor for Condensate Export Pump | N | M-E1 | 0.69 |  | S | 221 | 250 | 258.5083 | 0.884 | 95.2 | 0.85 | 10 | 0 | 0 | 0 | 0 | 23.2143 | 14.3869 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating 수정
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
D4 | MS | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-70-0001A-TH | Thyristor panel for Fuel Gas Heater | N | H1 | 0.69 |  | C | 153.1 | 184 | 162.0632 | 0.83207 | 95 | 1 | 100 | 161.1579 | 0 | 0 | 0 | 0 | 0 | Increased | 48KW -> 184KW |  |  | 20251216 Load Type 수정
20250105 IOM-ME(MS)-0005 Tag/Description 수정
20260211 VE-PR-044
D4 | MS | 4 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-HE-70-0001B-TH | Thyristor panel for Fuel Gas Heater | N | H1 | 0.69 |  | S | 153.1 | 184 | 162.0632 | 0.83207 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 16.1158 | 0 | Increased | 48KW -> 184KW |  |  | 20251216 Load Type 수정
20250105 IOM-ME(MS)-0005 Tag/Description 수정
20260211 VE-PR-044
C1 | MR | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-PA-20-0001A Motor | Motor for Condensate Recycle Pump | N | M-E1 | 0.69 |  | C | 219 | 250 | 259.8731 | 0.876 | 94.7 | 0.85 | 100 | 231.2566 | 143.32 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
20260105 IOM-ME(MR)-0007 Rating 수정
20260129 IOM-ECI(EL)-0016 Duty 수정 (CPR)
B | MR | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-PA-20-0001B Motor | Motor for Condensate Recycle Pump | N | M-E1 | 0.69 |  | S | 219 | 250 | 259.8731 | 0.876 | 94.7 | 0.85 | 10 | 0 | 0 | 0 | 0 | 23.1257 | 14.332 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
20260105 IOM-ME(MR)-0007 Rating 수정
B | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-31-1001 | 1st Stage FGC Recycle Cooler 1 Bay - Electric Heater | N | H2 | 0.69 |  | I | 12 | 15 | 13.2117 | 0.8 | 95 | 1 | 30 | 0 | 0 | 3.7895 | 0 | 0 | 0 | No Change |  |  |  | 20251216 Load Type 수정
20250105 IOM-ME(MS)-0005 Description 수정
B | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-31-1002 | 2nd Stage FGC Suction Cooler 1 Bay - Electric Heater | N | H2 | 0.69 |  | C | 28 | 35 | 30.8272 | 0.8 | 95 | 1 | 30 | 8.8421 | 0 | 0 | 0 | 0 | 0 | Increased | 15KW -> 25KW |  |  | 20251216 Load Type 수정
20250105 IOM-ME(MS)-0005 Description 수정
D4 | MR | 2 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-DM-43-0001A | Motor for Subsea MEG Injection Package | N | VSD-G2 | 0.69 |  | C | 104.5 | 110 | 113.9831 | 0.95 | 95 | 0.85 | 100 | 110 | 68.1719 | 0 | 0 | 0 | 0 | Decreased | 185KW -> 110KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (400->690)
20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 Rating 수정
20260317 IOM-ME(MR)-0016 VSD 반영
D4 | MR | 2 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-43-0001B | Motor for Subsea MEG Injection Package | N | VSD-G2 | 0.69 |  | I | 104.5 | 110 | 113.9831 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 33 | 20.4516 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 Rating 수정
20260317 IOM-ME(MR)-0016 VSD 반영
D4 | MR | 2 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-43-0001C | Motor for Subsea MEG Injection Package | N | VSD-G2 | 0.69 |  | S | 104.5 | 110 | 113.9831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 11 | 6.8172 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 Rating 수정
20260317 IOM-ME(MR)-0016 VSD 반영
C1 | MR | 1 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-36-0003B | Main Motor for Liquid Ring Compressor (70-KG-36-0003B) | N | VSD-G2 | 0.69 | VVVF | S | 320 | 355 | 367.8545 | 0.90141 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 33.6842 | 20.8756 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 (VVVF->SS) 수정
20260128 IOM-ME(MR)-0010 (SS->VVVF) 수정
D4 | MS | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UB-74-0001A-TH | Thyristor Panel for Electric Heater for N2 Generation Package | N | H2 | 0.69 |  | C | 20 | 25 | 25.9052 | 0.8 | 95 | 0.85 | 100 | 21.0526 | 13.0472 | 0 | 0 | 0 | 0 | Added |  |  |  | 20250105 IOM-ME(MS)-0005 Added
20260225 IOM-ME(MS)-0026 Voltage 수정 (400 -> 690)
D4 | MS | 4 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UB-74-0001B-TH | Thyristor Panel for Electric Heater for N2 Generation Package | N | H2 | 0.69 |  | S | 20 | 25 | 25.9052 | 0.8 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.1053 | 1.3047 | Added |  |  |  | 20250105 IOM-ME(MS)-0005 Added
20260129 IOM-ME(MS)-0011 Duty 수정
20260225 IOM-ME(MS)-0026 Voltage 수정 (400 -> 690)
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-A | Export Compressor Aftercooler (Bay 1 Fan 1) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-B | Export Compressor Aftercooler (Bay 1 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-C | Export Compressor Aftercooler (Bay 1 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-D | Export Compressor Aftercooler (Bay 2 Fan 1) | N | M-B1 | 0.69 |  | S | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.6157 | 1.1278 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-E | Export Compressor Aftercooler (Bay 2 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-F | Export Compressor Aftercooler (Bay 2 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-A | Export Compressor Aftercooler (Bay 1 Fan 1) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-B | Export Compressor Aftercooler (Bay 1 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-C | Export Compressor Aftercooler (Bay 1 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-D | Export Compressor Aftercooler (Bay 2 Fan 1) | N | M-B1 | 0.69 |  | S | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.6157 | 1.1278 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-E | Export Compressor Aftercooler (Bay 2 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-F | Export Compressor Aftercooler (Bay 2 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1001-A | 1st Stage FGC Recycle Cooler (Bay 1 Fan 1) | N | M-A1 | 0.69 |  | I | 4.4 | 5.5 | 6.7282 | 0.8 | 85.5 | 0.8 | 30 | 0 | 0 | 1.5439 | 1.1579 | 0 | 0 | Increased | 4KW -> 5.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1001-B | 1st Stage FGC Recycle Cooler (Bay 1 Fan 2) | N | M-A1 | 0.69 |  | I | 4.4 | 5.5 | 6.7282 | 0.8 | 85.5 | 0.8 | 30 | 0 | 0 | 1.5439 | 1.1579 | 0 | 0 | Increased | 4KW -> 5.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1001-C | 1st Stage FGC Recycle Cooler (Bay 1 Fan 3) | N | M-A1 | 0.69 |  | I | 4.4 | 5.5 | 6.7282 | 0.8 | 85.5 | 0.8 | 30 | 0 | 0 | 1.5439 | 1.1579 | 0 | 0 | Increased | 4KW -> 5.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1002-A | 2nd Stage FGC Suction Cooler (Bay 1 Fan 1) | N | M-A1 | 0.69 |  | C | 6 | 7.5 | 8.8438 | 0.8 | 88.7 | 0.8 | 100 | 6.7644 | 5.0733 | 0 | 0 | 0 | 0 | Increased | 4KW -> 7.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1002-B | 2nd Stage FGC Suction Cooler (Bay 1 Fan 2) | N | M-A1 | 0.69 |  | C | 6 | 7.5 | 8.8438 | 0.8 | 88.7 | 0.8 | 100 | 6.7644 | 5.0733 | 0 | 0 | 0 | 0 | Increased | 4KW -> 7.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 3 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1002-C | 2nd Stage FGC Suction Cooler (Bay 1 Fan 3) | N | M-A1 | 0.69 |  | S | 6 | 7.5 | 8.8438 | 0.8 | 88.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.67644 | 0.50733 | Increased | 4KW -> 7.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 4 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-72-0001-A | Heating Medium Dump Cooler (Bay 1 Fan 1) | N | M-B1 | 0.69 |  | I | 24 | 30 | 33.4197 | 0.8 | 91.6 | 0.82 | 30 | 0 | 0 | 7.8603 | 5.4865 | 0 | 0 | No Change |  | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 4 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-72-0001-B | Heating Medium Dump Cooler (Bay 1 Fan 2) | N | M-B1 | 0.69 |  | S | 24 | 30 | 33.4197 | 0.8 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 2.6201 | 1.8288 | No Change |  | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-72-0001-C | Heating Medium Dump Cooler (Bay 1 Fan 3) | N | M-B1 | 0.69 |  | I | 24 | 30 | 33.4197 | 0.8 | 91.6 | 0.82 | 30 | 0 | 0 | 7.8603 | 5.4865 | 0 | 0 | No Change |  | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V)
Tag 수정 (by EL)
20260129 IOM-ME(MS)-0011 Rating
20260203 (△-Y)
20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D4 | MS | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A1 | MEG Regeneration Package | N | VSD-G2 | 0.69 | VVVF | C | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 100 | 10.5263 | 6.5236 | 0 | 0 | 0 | 0 | Decreased | 50KW -> 10KW |  |  | 20250105 IOM-ME(MS)-0005 Added
[7 empty] | - Overhead Condenser (Air cooler) | [22 empty] | Tag 수정 (by EL)
20260225 IOM-ME(MS)-0026 VSD (임의 반영)
20260317 IOM-ME(MS)-0032 description 수정
D4 | MS | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A2 | MEG Regeneration Package | N | VSD-G2 | 0.69 | VVVF | C | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 100 | 10.5263 | 6.5236 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MS)-0032 Added
- Overhead Condenser (Air cooler)
D4 | MS | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A3 | MEG Regeneration Package | N | VSD-G2 | 0.69 | VVVF | S | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.0526 | 0.65236 | Added |  |  |  | 20260317 IOM-ME(MS)-0032 Added
- Overhead Condenser (Air cooler)
D3 | MS | 4 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A - SP | MEG Regeneration Package | N | VSD-G2 | 0.69 | VVVF | S | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.0526 | 0.65236 | Added |  |  |  | 20260225 IOM-ME(MS)-0026 추가 (임의 반영)
[7 empty] | - Overhead Condenser (Air cooler) - Spare | [22 empty] | 20260225 IOM-ME(MS)-0026 VSD (임의 반영)
D3 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 | Export Compressor _ Main LO Pump Motor | N | M-A1 | 0.4 |  | C | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 100 | 28.4211 | 17.6138 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | Main Lube Oil Pump Motor | [23 empty] | 20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 | Export Compressor _ Standby LO Pump Motor | N | M-A1 | 0.4 |  | S | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.8421 | 1.7614 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | S/b Lube Oil Pump Motor | [23 empty] | 20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 | LO Heater for Export Compressor | N | H2 | 0.4 |  | I | 38.7 | 43 | 76.8609 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 12.2211 | 7.5739 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | LO reservoir Heater | [23 empty] | 20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 용량 수정
D4 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 | Export Compressor _ LO cooler Fan Motor 1 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | LO Cooler Fan Motor 1 | [23 empty] | 20251216 Load Type 수정
20260105 IOM-ME(MR)-0007 Rating 수정
20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 | Export Compressor _ LO cooler Fan Motor 2 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | LO Cooler Fan Motor 2 | [23 empty] | 20251216 Load Type 수정
20260105 IOM-ME(MR)-0007 Rating, Duty 수정
20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 | Export Compressor _ LO cooler Fan Motor 3 | N | M-A1 | 0.4 |  | S | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.94737 | 0.58713 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
[6 empty] | LO Cooler Fan Motor 3 | [23 empty] | 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
B | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 | Export Compressor _ Oil Mist Eliminator Fan Motor | N | M-A1 | 0.4 |  | C | 0.9 | 1 | 1.7875 | 0.9 | 95 | 0.85 | 100 | 0.94737 | 0.58713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
Oil Mist Eliminator Fan Motor
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 | Export Compressor _ VFD (E-house Low Voltage Power Disctribution for HVAC, water circulation unit, F&G) | N | F | 0.4 |  | C | 72 | 80 | 142.997 | 0.9 | 95 | 0.85 | 100 | 75.7895 | 46.9701 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
[6 empty] | E-House (incl. VFD Panel) | [23 empty] | 20260317 IOM-ME(MR)-0016 수정
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 | Export Compressor _ VFD (Cooling Systems - Chiller Package) | N | M-B1 | 0.4 |  | C | 90 | 100 | 178.7462 | 0.9 | 95 | 0.85 | 100 | 94.7368 | 58.7126 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MR)-0016 추가
VFD _ Chiller
D3 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 | Export Compressor _ Main LO Pump Motor | N | M-A1 | 0.4 |  | C | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 100 | 28.4211 | 17.6138 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | Main Lube Oil Pump Motor | [23 empty] | 20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 | Export Compressor _ Standby LO Pump Motor | N | M-A1 | 0.4 |  | S | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.8421 | 1.7614 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | S/b Lube Oil Pump Motor | [23 empty] | 20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 | LO Heater for Export Compressor | N | H2 | 0.4 |  | I | 38.7 | 43 | 76.8609 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 12.2211 | 7.5739 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | LO reservoir Heater | [23 empty] | 20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 용량 수정
D4 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 | Export Compressor _ LO cooler Fan Motor 1 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | LO Cooler Fan Motor 1 | [23 empty] | 20251216 Load Type 수정
20260105 IOM-ME(MR)-0007 Rating 수정
20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 | Export Compressor _ LO cooler Fan Motor 2 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
[6 empty] | LO Cooler Fan Motor 2 | [23 empty] | 20251216 Load Type 수정
20260105 IOM-ME(MR)-0007 Rating, Duty 수정
20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 | Export Compressor _ LO cooler Fan Motor 3 | N | M-A1 | 0.4 |  | S | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.94737 | 0.58713 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
[6 empty] | LO Cooler Fan Motor 3 | [23 empty] | 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
B | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 | Export Compressor _ Oil Mist Eliminator Fan Motor | N | M-A1 | 0.4 |  | C | 0.9 | 1 | 1.7875 | 0.9 | 95 | 0.85 | 100 | 0.94737 | 0.58713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
Oil Mist Eliminator Fan Motor
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 | Export Compressor _ VFD (E-house Low Voltage Power Disctribution for HVAC, water circulation unit, F&G) | N | F | 0.4 |  | C | 72 | 80 | 142.997 | 0.9 | 95 | 0.85 | 100 | 75.7895 | 46.9701 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
[6 empty] | E-House (incl. VFD Panel) | [23 empty] | 20260317 IOM-ME(MR)-0016 수정
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 | Export Compressor _ VFD (Cooling Systems - Chiller Package) | N | M-B1 | 0.4 |  | C | 90 | 100 | 178.7462 | 0.9 | 95 | 0.85 | 100 | 94.7368 | 58.7126 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MR)-0016 추가
VFD _ Chiller
A | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Aux Lube Oil Pump Motor | Aux LO Pump for Flash Gas Compressor | N | M-A1 | 0.4 |  | I | 4.95 | 5.5 | 9.831 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.5632 | 0.96876 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
A | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Main CW Pump Motor | Main CW Pump Motor for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 100 | 7.1053 | 4.4034 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
A | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Aux CW Pump Motor | Aux CW Pump Motor for Flash Gas Compressor | N | M-A1 | 0.4 |  | S | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.71053 | 0.44034 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
A | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-LO Heater | LO Heater for Flash Gas Compressor | N | H2 | 0.4 |  | I | 2.7 | 3 | 5.3624 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 0.85263 | 0.52841 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
D3 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Coolant Heater | Coolant Heater for Flash Gas Compressor | N | H2 | 0.4 |  | I | 13.5 | 15 | 26.8119 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 4.2632 | 2.6421 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 용량 수정
A | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Electric Barring Device Motor | Electric Barring Device Motor for Flash Gas Compressor | N | M-A1 | 0.4 |  | I | 1.35 | 1.5 | 2.6812 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 0.42632 | 0.26421 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
A | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-LO Cooler Fan Motor 1 | LO Cooler Fan Motor 1 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 100 | 7.1053 | 4.4034 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
D3 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-LO Cooler Fan Motor 2 | LO Cooler Fan Motor 2 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 100 | 7.1053 | 4.4034 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 description, duty 수정
D3 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-LO Cooler Fan Motor 3 | LO Cooler Fan Motor 3 for Flash Gas Compressor | N | M-A1 | 0.4 |  | S | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.71053 | 0.44034 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 1 | CW Console Cooler Fan Motor 1 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 9.9 | 11 | 19.6621 | 0.9 | 95 | 0.85 | 100 | 10.4211 | 6.4584 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
D3 | MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 2 | CW Console Cooler Fan Motor 2 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 9.9 | 11 | 19.6621 | 0.9 | 95 | 0.85 | 100 | 10.4211 | 6.4584 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260225 IOM-ME(MR)-0014 duty 수정
D3 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 3 | CW Console Cooler Fan Motor 3 for Flash Gas Compressor | N | M-A1 | 0.4 |  | S | 9.9 | 11 | 19.6621 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.0421 | 0.64584 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Cylinder Lubricator Heater | Cylinder Lubricator Heater for Flash Gas Compressor | N | H2 | 0.4 |  | I | 0.9 | 1 | 1.7875 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 0.28421 | 0.17614 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0001A Hydraulic Motor | Diesel Firewater Pump A Hydraulic Motor | N | M-A1 | 0.4 |  | S | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.47368 | 0.29356 | Decreased | 15KW -> 5KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
D3 | MR | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0001A Panel | Diesel Firewater Pump A Enclosure Ventilation Fan Motor | N | M-A1 | 0.4 |  | S | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.47368 | 0.29356 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001B Hydraulic Motor | Diesel Firewater Pump B Hydraulic Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Decreased | 15KW -> 5KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
D3 | MR | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001B Panel | Diesel Firewater Pump B Enclosure Ventilation Fan Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001C Hydraulic Motor | Diesel Firewater Pump C Hydraulic Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Decreased | 15KW -> 5KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
D3 | MR | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001C Panel | Diesel Firewater Pump C Enclosure Ventilation Fan Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
| EL | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-HF-01-0002 | Fire water pump control panel | N | F | 0.4 |  | C | 3.8 | 5 | 8.9373 | 0.76 | 95 | 0.85 | 100 | 4 | 2.479 | 0 | 0 | 0 | 0 | No Change |  |  |  | FEED
D3 | MR | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0003A(Main Motor Power) | Firewater Jockey Pump A Motor | N | M-B1 | 0.4 |  | C | 65 | 75 | 136.2103 | 0.86667 | 93.5 | 0.85 | 100 | 69.5187 | 43.0838 | 0 | 0 | 0 | 0 | Increased | 55KW -> 75KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating 수정
20260225 IOM-ME(MR)-0014 Description / Load Type 수정
D3 | MR | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0003B(Main Motor Power) | Firewater Jockey Pump B Motor | N | M-B1 | 0.4 |  | S | 65 | 75 | 136.2103 | 0.86667 | 93.5 | 0.85 | 10 | 0 | 0 | 0 | 0 | 6.9519 | 4.3084 | Increased | 55KW -> 75KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating 수정
20260225 IOM-ME(MR)-0014 Description / Load Type 수정
B | MR | 1 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0001A Motor | Motor for Closed Drains Drum Booster Pump | N | M-A1 | 0.4 |  | I | 1.5 | 3.7 | 7.1412 | 0.40541 | 91.2 | 0.82 | 30 | 0 | 0 | 0.49342 | 0.34441 | 0 | 0 | Decreased | 4KW -> 3.7KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating 수정
B | MR | 1 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0001A Seal Motor | Motor for Closed Drains Drum Booster Pump- Seal Circulation Pump | N | M-A1 | 0.4 |  | I | 0.4 | 0.55 | 1.0615 | 0.72727 | 91.2 | 0.82 | 30 | 0 | 0 | 0.13158 | 0.091843 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 1 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0001B Motor | Motor for Closed Drains Drum Booster Pump | N | M-A1 | 0.4 |  | S | 1.5 | 3.7 | 7.1412 | 0.40541 | 91.2 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.16447 | 0.1148 | Decreased | 4KW -> 3.7KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating 수정
B | MR | 1 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0001B Seal Motor | Motor for Closed Drains Drum Booster Pump- Seal Circulation Pump | N | M-A1 | 0.4 |  | I | 0.4 | 0.55 | 1.0615 | 0.72727 | 91.2 | 0.82 | 30 | 0 | 0 | 0.13158 | 0.091843 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B2 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0004A Motor | Motor for Off spec Water Recycle Pump | N | M-A1 | 0.4 |  | I | 6.02 | 7.5 | 15.2555 | 0.80267 | 88.7 | 0.8 | 30 | 0 | 0 | 2.0361 | 1.5271 | 0 | 0 | Increased | 5.5KW -> 7.5KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating, WBS 수정
20260108 IOM-ECI(EL)-0007 CPR 답변 반영
B | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0004B Motor | Motor for Off spec Water Recycle Pump | N | M-A1 | 0.4 |  | S | 6.02 | 7.5 | 15.2555 | 0.80267 | 88.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.67869 | 0.50902 | Increased | 5.5KW -> 7.5KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20260105 IOM-ME(MR)-0007 Rating, WBS 수정
B | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0005A Motor | Motor for Open Drains Treatment Pump | N | M-A1 | 0.4 |  | I | 11.4 | 15 | 30.511 | 0.76 | 88.7 | 0.8 | 30 | 0 | 0 | 3.8557 | 2.8918 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0005B Motor | Motor for Open Drains Treatment Pump | N | M-A1 | 0.4 |  | S | 11.4 | 15 | 30.511 | 0.76 | 88.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 1.2852 | 0.96392 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
D4 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven Main LO Pump | N | M-A1 | 0.4 |  | C | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 100 | 5.5 | 3.4086 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven Aux. LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
20260317 IOM-ME(MR)-0016 Rating 수정
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven LO Air Cooler Fan A | N | M-A1 | 0.4 |  | C | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 100 | 3 | 1.8592 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven LO Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven Lubricator | N | M-A1 | 0.4 |  | C | 1.9 | 2 | 3.5749 | 0.95 | 95 | 0.85 | 100 | 2 | 1.2395 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | LO Heater | N | M-A1 | 0.4 |  | I | 3 | 3 | 5.3624 | 1 | 95 | 0.85 | 30 | 0 | 0 | 0.94737 | 0.58713 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D4 | MR | 2 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven Main LO Pump | N | M-A1 | 0.4 |  | I | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 1.65 | 1.0226 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 2 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven Aux. LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
20260317 IOM-ME(MR)-0016 Rating 수정
D3 | MR | 2 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven LO Air Cooler Fan A | N | M-A1 | 0.4 |  | I | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 0.9 | 0.55777 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven LO Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven Lubricator | N | M-A1 | 0.4 |  | I | 1.9 | 2 | 3.5749 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 0.6 | 0.37185 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | LO Heater | N | M-A1 | 0.4 |  | I | 3 | 3 | 5.3624 | 1 | 95 | 0.85 | 30 | 0 | 0 | 0.94737 | 0.58713 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D4 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven Main LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven Aux. LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
20260317 IOM-ME(MR)-0016 Rating 수정
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven LO Air Cooler Fan A | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven LO Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven Lubricator | N | M-A1 | 0.4 |  | S | 1.9 | 2 | 3.5749 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.2 | 0.12395 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | LO Heater | N | M-A1 | 0.4 |  | S | 3 | 3 | 5.3624 | 1 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.31579 | 0.19571 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
| MR | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-31-1003 | 1st Stage FGC Suction Scrubber Pump Motor - Train 1 | N | M-A1 | 0.4 |  | I | 0.032 | 0.75 | 1.6624 | 0.042667 | 81.4 | 0.8 | 30 | 0 | 0 | 0.011794 | 0.0088452 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-43-0001A | Rich MEG Pump | N | M-A1 | 0.4 |  | C | 8.75 | 11 | 21.5616 | 0.79545 | 89.8 | 0.82 | 100 | 9.7439 | 6.8013 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0001B | Rich MEG Pump | N | M-A1 | 0.4 |  | S | 8.75 | 11 | 21.5616 | 0.79545 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.97439 | 0.68013 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
B3 | MS | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-C | MEG Regeneration Package | N | M-A1 | 0.4 |  | C | 5.5 | 5.5 | 11.3149 | 1 | 87.7 | 0.8 | 100 | 6.2714 | 4.7035 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 Description 수정
[7 empty] | - Lean MEG Pump A | [22 empty] | Tag 수정 (by EL)
B3 | MS | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-D | MEG Regeneration Package | N | M-A1 | 0.4 |  | S | 5.5 | 5.5 | 11.3149 | 1 | 87.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.62714 | 0.47035 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 Description 수정
[7 empty] | - Lean MEG Pump B | [22 empty] | Tag 수정 (by EL)
D3 | MS | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-E | MEG Regeneration Package | N | M-A1 | 0.4 |  | C | 30 | 30 | 58.2852 | 1 | 90.6 | 0.82 | 100 | 33.1126 | 23.1127 | 0 | 0 | 0 | 0 | Increased | 15KW -> 30KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정
[7 empty] | - Reflux Pump A | [22 empty] | Tag 수정 (by EL)
20260225 IOM-ME(MS)-0026 Rating 수정
D3 | MS | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-F | MEG Regeneration Package | N | M-A1 | 0.4 |  | S | 30 | 30 | 58.2852 | 1 | 90.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.3113 | 2.3113 | Increased | 15KW -> 30KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정
[7 empty] | - Reflux Pump B | [22 empty] | Tag 수정 (by EL)
20260225 IOM-ME(MS)-0026 Rating 수정
D3 | MS | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-G | MEG Regeneration Package | N | M-A1 | 0.4 |  | I | 7.55 | 7.55 | 15.7296 | 1 | 86.6 | 0.8 | 30 | 0 | 0 | 2.6155 | 1.9616 | 0 | 0 | Increased | 4KW -> 7.55KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정
[7 empty] | - Hydrocarbon Recovery Pump A | [22 empty] | Tag 수정 (by EL)
20260225 IOM-ME(MS)-0026 Rating 수정
D3 | MS | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-H | MEG Regeneration Package | N | M-A1 | 0.4 |  | S | 7.55 | 7.55 | 15.7296 | 1 | 86.6 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.87182 | 0.65387 | Increased | 4KW -> 7.55KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정
[7 empty] | - Hydrocarbon Recovery Pump B | [22 empty] | Tag 수정 (by EL)
20260225 IOM-ME(MS)-0026 Rating 수정
| MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-43-0003A | Lean MEG Transfer Pump | N | M-A1 | 0.4 |  | C | 2.5 | 7.5 | 15.8265 | 0.33333 | 85.5 | 0.8 | 100 | 2.924 | 2.193 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0003B | Lean MEG Transfer Pump | N | M-A1 | 0.4 |  | S | 2.5 | 7.5 | 15.8265 | 0.33333 | 85.5 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.2924 | 0.2193 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0004 | MEG Offloading Pump | N | M-A1 | 0.4 |  | I | 3.63 | 7.5 | 15.8265 | 0.484 | 85.5 | 0.8 | 30 | 0 | 0 | 1.2737 | 0.95526 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
C3 | EL | 7 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0054 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Gate house - Indoor (70-IG-62-0054) | N | L | 0.4 |  | C | 2.1 | 5 | 8.9373 | 0.42 | 95 | 0.85 | 100 | 2.2105 | 1.37 | 0 | 0 | 0 | 0 |  |  |  | MAIN GATE HOUSE | 20251216 FEED EQ LIST Added
C3 | EL | 7 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0055 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Access control building Security HUT 02 - Indoor (70-IG-62-0055) | N | L | 0.4 |  | C | 2.1 | 5 | 8.9373 | 0.42 | 95 | 0.85 | 100 | 2.2105 | 1.37 | 0 | 0 | 0 | 0 |  |  |  | SECURITY HUT 02 | FEED
C3 | EL | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0056A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building - Indoor A (70-IG-62-0056A) | N | L | 0.4 |  | C | 26.5 | 30 | 53.6239 | 0.88333 | 95 | 0.85 | 100 | 27.8947 | 17.2876 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0056B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building - Indoor B (70-IG-62-0056B) | N | L | 0.4 |  | C | 29 | 30 | 53.6239 | 0.96667 | 95 | 0.85 | 100 | 30.5263 | 18.9185 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 6 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0059A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Workshop & Warehouse - Indoor A (70-IG-62-0059A) | N | L | 0.4 |  | C | 24.5 | 30 | 53.6239 | 0.81667 | 95 | 0.85 | 100 | 25.7895 | 15.9829 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 6 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0059B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Workshop & Warehouse - Indoor B (70-IG-62-0059B) | N | L | 0.4 |  | C | 26 | 30 | 53.6239 | 0.86667 | 95 | 0.85 | 100 | 27.3684 | 16.9614 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 6 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0060 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Adminstration Building - Indoor (70-IG-62-0060) | N | L | 0.4 |  | C | 24 | 30 | 53.6239 | 0.8 | 95 | 0.85 | 100 | 25.2632 | 15.6567 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 6 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0061 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building (Laboratory room) - Indoor (70-IG-62-0061) | N | L | 0.4 |  | C | 40 | 50 | 89.3731 | 0.8 | 95 | 0.85 | 100 | 42.1053 | 26.0945 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0062A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Substation - Indoor A (70-IG-62-0062A) | N | L | 0.4 |  | C | 23 | 30 | 53.6239 | 0.76667 | 95 | 0.85 | 100 | 24.2105 | 15.0043 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0062B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Substation - Indoor B (70-IG-62-0062B) | N | L | 0.4 |  | C | 24 | 30 | 53.6239 | 0.8 | 95 | 0.85 | 100 | 25.2632 | 15.6567 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0064A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - ITR East-Utilities - Indoor A (70-IG-62-0064A) | N | L | 0.4 |  | C | 28 | 30 | 53.6239 | 0.93333 | 95 | 0.85 | 100 | 29.4737 | 18.2661 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0064B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - ITR East-Utilities - Indoor B (70-IG-62-0064B) | N | L | 0.4 |  | C | 25 | 30 | 53.6239 | 0.83333 | 95 | 0.85 | 100 | 26.3158 | 16.3091 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-66-0002 | 0.4/0.42kV Dry type Transformer for 400V Normal Welding Outlet DB- Outdoor A (70-IG-66-0002) | N | F | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 0 | 0 | 59.7267 | 0 |  |  |  |  | 20260120 Added_Franca
C4 | EL | 7 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0099 | 0.4/0.42kV Dry type Transformer for 400/230V Normal DB for EV Charging (70-IG-62-0099) | N | L | 0.4 | [9 empty] | 0 | 0 | 12.6 | 7.8088 | 0 | 0 |  |  |  |  | 20260209 추가
B3 | MS | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-71-0001-A | Diesel Transfer and Filtration Package Pump Motor A | N | M-A1 | 0.4 |  | I | 2.2 | 2.2 | 4.7085 | 1 | 84.3 | 0.8 | 30 | 0 | 0 | 0.78292 | 0.58719 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 Tag 수정
Tag 수정 (by EL)
B3 | MS | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-71-0001-B | Diesel Transfer and Filtration Package Pump Motor B | N | M-A1 | 0.4 |  | S | 2.2 | 2.2 | 4.7085 | 1 | 84.3 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.26097 | 0.19573 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 Tag 수정
Tag 수정 (by EL)
| MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-72-0001A | Heating Medium Circulation Pump | N | M-B1 | 0.4 |  | C | 79.2 | 90 | 163.4524 | 0.88 | 93.5 | 0.85 | 100 | 84.7059 | 52.496 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-72-0001B | Heating Medium Circulation Pump | N | M-B1 | 0.4 |  | S | 79.2 | 90 | 163.4524 | 0.88 | 93.5 | 0.85 | 10 | 0 | 0 | 0 | 0 | 8.4706 | 5.2496 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
D4 | MS | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-72-0001A | Fired Heater A FD Fan | N | F | 0.4 |  | C | 30 | 30 | 53.6239 | 1 | 95 | 0.85 | 100 | 31.5789 | 19.5709 | 0 | 0 | 0 | 0 | Increased | 10KW -> 30KW |  |  | 20250105 IOM-ME(MS)-0005 Tag/Description/Rating 수정
[6 empty] | (70-HF-72-0001A) | [23 empty] | 20260317 Tag 오류 수정
20260317 IOM-ME(MS)-0032 용량 수정
D4 | MS | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-72-0001B | Fired Heater B FD Fan | N | F | 0.4 |  | C | 30 | 30 | 53.6239 | 1 | 95 | 0.85 | 100 | 31.5789 | 19.5709 | 0 | 0 | 0 | 0 | Increased / Duty | 10KW -> 30KW / S -> C |  |  | 20250105 IOM-ME(MS)-0005 Tag/Description/Rating 수정
[6 empty] | (70-HF-72-0001B) | [23 empty] | 20260317 Tag 오류 수정
20260317 IOM-ME(MS)-0032 용량 수정
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Pump A | Motor for Pour Point Depressant Injection Package | N | M-A1 | 0.4 |  | C | 1.43 | 1.5 | 2.6812 | 0.95333 | 95 | 0.85 | 100 | 1.5053 | 0.93288 | 0 | 0 | 0 | 0 | Increased / Duty | 0.75KW -> 1.5KW / I -> C |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Pump B | Motor for Pour Point Depressant Injection Package | N | M-A1 | 0.4 |  | S | 1.43 | 1.5 | 2.6812 | 0.95333 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.15053 | 0.093288 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007_Duty 수정
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Agitator | Motor for Agitator | N | M-A1 | 0.4 |  | C | 3.8 | 4 | 7.1498 | 0.95 | 95 | 0.85 | 100 | 4 | 2.479 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Filling Pump | Motor for Filling Pump | N | M-A1 | 0.4 |  | I | 2.09 | 2.2 | 3.9324 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 0.66 | 0.40903 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Pump A | Motor for Corrosion Inhibitor Injection Package | N | M-A1 | 0.4 |  | C | 0.24 | 0.25 | 0.44687 | 0.96 | 95 | 0.85 | 100 | 0.25263 | 0.15657 | 0 | 0 | 0 | 0 | Decreased | 0.75KW -> 0.25KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Pump B | Motor for Corrosion Inhibitor Injection Package | N | M-A1 | 0.4 |  | S | 0.24 | 0.25 | 0.44687 | 0.96 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.025263 | 0.015657 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007_Duty 수정
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Agitator | Motor for Agitator | N | M-A1 | 0.4 |  | C | 0.35 | 0.37 | 0.66136 | 0.94595 | 95 | 0.85 | 100 | 0.36842 | 0.22833 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Filling Pump | Motor for Filling Pump | N | M-A1 | 0.4 |  | I | 0.71 | 0.75 | 1.3406 | 0.94667 | 95 | 0.85 | 30 | 0 | 0 | 0.22421 | 0.13895 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-75-0001-Pump A | Motor for MEG Injection Package | N | M-A1 | 0.4 |  | C | 20.9 | 22 | 39.3242 | 0.95 | 95 | 0.85 | 100 | 22 | 13.6344 | 0 | 0 | 0 | 0 | Increased | 5KW -> 22KW |  |  | 20251202 IOM-ME(MR)-0003 수정
20251216 Load Type 수정
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-75-0001-Pump B | Motor for MEG Injection Package | N | M-A1 | 0.4 |  | S | 20.9 | 22 | 39.3242 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.2 | 1.3634 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007_Duty 수정
20260128 IOM-ME(MR)-0010 Rating 수정
| MR | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-85-0001A | Utility Water Pump A Motor | N | M-A1 | 0.4 |  | S | 5.8 | 11 | 21.5616 | 0.52727 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.64588 | 0.45083 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-85-0001B | Utility Water Pump B Motor | N | M-A1 | 0.4 |  | C | 5.8 | 11 | 21.5616 | 0.52727 | 89.8 | 0.82 | 100 | 6.4588 | 4.5083 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 1 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-28-0007A | Closed Drains Pump | N | M-A1 | 0.4 |  | I | 11.3 | 15 | 29.4022 | 0.75333 | 89.8 | 0.82 | 30 | 0 | 0 | 3.7751 | 2.635 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 1 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-28-0007B | Closed Drains Pump | N | M-A1 | 0.4 |  | S | 11.3 | 15 | 29.4022 | 0.75333 | 89.8 | 0.82 | 30 | 0 | 0 | 0 | 0 | 3.7751 | 2.635 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
D3 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-Liquid Ring Recirculation Pump | Motor for Liquid Ring Recirculation Pump A | N | M-A1 | 0.4 |  | C | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 100 | 15.0334 | 10.4934 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-Liquid Ring Recirculation Pump | Motor for Liquid Ring Recirculation Pump B | N | M-A1 | 0.4 |  | S | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.5033 | 1.0493 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-Liquid Ring Air Cooler | Motor for Liquid Ring Air Cooler Fan A | N | M-A1 | 0.4 |  | C | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 100 | 15.0334 | 10.4934 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-Liquid Ring Air Cooler | Motor for Liquid Ring Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.5033 | 1.0493 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-LO Heater for 70-KG-36-0003A | LO Heater for Liquid Ring Compressor (70-KG-36-0003A) | N | H2 | 0.4 |  | I | 2.7 | 3 | 5.8804 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 0.902 | 0.6296 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-LO Heater for 70-KG-36-0003B | LO Heater for Liquid Ring Compressor (70-KG-36-0003B) | N | H2 | 0.4 |  | I | 2.7 | 3 | 5.8804 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 0.902 | 0.6296 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.1 | Aeration system(Rotor) A for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.1.2 | Aeration system(Rotor) B for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.3 | Aeration system(Rotor) C for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.1.4 | Aeration system(Rotor) D for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.5 | Skimmer for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
20260128 IOM-ME(MR)-0010 Rating 수정
D4 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.2.1 | FLOAT OILY SLUDGE PUMP A (included in 70-UU-28-0001) | N | M-A1 | 0.4 |  | C | 1.76 | 2.2 | 4.3123 | 0.8 | 89.8 | 0.82 | 100 | 1.9599 | 1.368 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
20260317 IOM-ME(MR)-0016 Tag/Description 수정
D4 | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.2.2 | FLOAT OILY SLUDGE PUMP A (included in 70-UU-28-0001) | N | M-A1 | 0.4 |  | C | 1.76 | 2.2 | 4.3123 | 0.8 | 89.8 | 0.82 | 100 | 1.9599 | 1.368 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MR)-0016 Added
B | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 3.1 | Dosing Pump_A_Demulsifying Chemical Dosing System | N | M-A1 | 0.4 |  | C | 0.32 | 0.4 | 0.78406 | 0.8 | 89.8 | 0.82 | 100 | 0.35635 | 0.24873 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 3.2 | Dosing Pump_B_Demulsifying Chemical Dosing System | N | M-A1 | 0.4 |  | S | 0.32 | 0.4 | 0.78406 | 0.8 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.035635 | 0.024873 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 4 | Agitator_Demulsifying Chemical Dosing System | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
A | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JC-78-0003 | Overhead Crane - Workshop Building (10 Te SWL) | N | F | 0.4 |  | I | 9 | 10 | 19.6015 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 3.0067 | 2.0987 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
20251216 Load Type 수정
D | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JH-78-0001 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
D | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-JH-78-0002 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
D | MR | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JH-78-0003 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
D | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-JH-78-0004 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
B | MR | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | EV-0001 (Temp) | Elevator | Em | F | 0.4 |  | I | 15.2 | 18 | 35.2827 | 0.84444 | 89.8 | 0.82 | 30 | 0 | 0 | 5.078 | 3.5444 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-CEMS-72-0001A (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (Lighting & etc. for 70-UZ-72-0001A) | N | F | 0.4 |  | C | 1.79 | 1.79 | 3.5087 | 1 | 89.8 | 0.82 | 100 | 1.9933 | 1.3913 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-CEMS-72-0001B (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (Lighting & etc. for 70-UZ-72-0001B) | N | F | 0.4 |  | C | 1.79 | 1.79 | 3.5087 | 1 | 89.8 | 0.82 | 100 | 1.9933 | 1.3913 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-CEMS-72-0001C (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001A) - Primary | N | F | 0.4 |  | C | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 100 | 12.5835 | 8.7834 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-CEMS-72-0001D (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001B) - Primary | N | F | 0.4 |  | C | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 100 | 12.5835 | 8.7834 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-CEMS-72-0001E (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001A) - Redundant | N | F | 0.4 |  | S | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.2584 | 0.87834 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-CEMS-72-0001F (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001B) - Redundant | N | F | 0.4 |  | S | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.2584 | 0.87834 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-26-0001 | Analyser House for Condensate Export Metering Package (Lighting & etc.) | N | F | 0.4 |  | C | 2.4 | 2.4 | 4.7044 | 1 | 89.8 | 0.82 | 100 | 2.6726 | 1.8655 | 0 | 0 | 0 | 0 | Added |  |  | 26 (아래 Plotplan 상 Location 참조) | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 03 (35) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0002/0003/0004 | Analyser House for SCP Export, DGN Export and Buy-back Gas Metering Package (Lighting & etc.) | N | F | 0.4 |  | C | 2.4 | 2.4 | 4.7044 | 1 | 89.8 | 0.82 | 100 | 2.6726 | 1.8655 | 0 | 0 | 0 | 0 | Added |  |  | 35 (아래 Plotplan 상 Location 참조) | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 03 (26) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-26-0001 (HVAC) | Analyser House for Condensate Export Metering Package (HVAC) - Primary | N | F | 0.4 |  | C | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 100 | 22.2717 | 15.5458 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (35) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0002/0003/0004 (HVAC) | Analyser House for SCP Export, DGN Export and Buy-back Gas Metering Package (HVAC) - Primary | N | F | 0.4 |  | C | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 100 | 22.2717 | 15.5458 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-26-0001 (HVAC) | Analyser House for Condensate Export Metering Package (HVAC) - Redundant | N | F | 0.4 |  | S | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 2.2272 | 1.5546 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (35) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0002/0003/0004 (HVAC) | Analyser House for SCP Export, DGN Export and Buy-back Gas Metering Package (HVAC) - Redundant | N | F | 0.4 |  | S | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 2.2272 | 1.5546 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D | EL | 12 | 70-IK-61-0002 | A | 70-IK-61-0002A | 82-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Production Inlet | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | B | 70-IK-61-0002B | 83-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Gas Export | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | A | 70-IK-61-0002A | 84-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Condensate | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | B | 70-IK-61-0002B | 86-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - MEG | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | A | 70-IK-61-0002A | 87-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Domestic Gas Export | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1001 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1002 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1011 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1012 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1013 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1014 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 4 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1003 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 4 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1004 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 3 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1005 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 03 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 3 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1006 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 03 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 2 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1007 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 02 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 2 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1008 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 02 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 1 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1009 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 01 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 1 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1010 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 01 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 5 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1015 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 5 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1016 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
C4 | EL | 7 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 1 | EV Charging - 1 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 7 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 2 | EV Charging - 2 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 7 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 3 | EV Charging - 3 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 7 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 4 | EV Charging - 4 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 7 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 5 | EV Charging - 5 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 7 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 6 | EV Charging - 6 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1001 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (1 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1002 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (2 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1003 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (3 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1004 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (4 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1005 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (5 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1006 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (6 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1007 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (7 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1008 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (8 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1009 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (9 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1010 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (10 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1011 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (11 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1012 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (12 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1013 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (13 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1014 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (14 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1015 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (15 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1016 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (16 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2001 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (1 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2002 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (2 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2003 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (3 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2004 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (4 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2005 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (5 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2006 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (6 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2007 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (7 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2008 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (8 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2009 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (9 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2010 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (10 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3001 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (1 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3002 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (2 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3003 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (3 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3004 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (4 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3005 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (5 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3006 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (6 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3007 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (7 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3008 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (8 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3009 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (9 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3010 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (10 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4001 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (1 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4002 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (2 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4003 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (3 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4004 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (4 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0001 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0 |  |  |  | AT THE INLET OF 70-VP-10-0001 | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0002 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0 |  |  |  | AT THE INLET OF 70-VP-10-0001 | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0003 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-VP-10-0001 TO SLUG CATCHERS | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0004 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-VP-10-0001 TO SLUG CATCHERS | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0005 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 3.87 | 4.3 | 6.81 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 1.29 | 0.90043 | 0 | 0 |  |  |  | FROM SUBSEA PRODUCTION FLOWLINE TO CHOKE VALVES | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 03 (25) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-25-0021 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-UN-26-0001 TO 70-VP-25-0001 | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 03 (25) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-25-0022 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-UN-26-0001 TO SD2 AT SANGACHAL TERMINAL | 20260108 IOM-ECI(EL)-0007 Added
C | EL | 1 | 70-IG-66-0001 |  | 70-IG-66-0001 | 01-WO-0001 | Welding Socket Outlet X 2EA (01-WO-01 & 01-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
D | EL | 1 | 70-IG-66-0001 |  | 70-IG-66-0001 | 01-WO-0002 | Welding Socket Outlet X 2EA (01-WO-03 & 01-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  | Flare stack area에 2ea 반영 |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 2 | 70-IG-66-0001 |  | 70-IG-66-0001 | 02-WO-0001 | Welding Socket Outlet X 2EA (02-WO-01 & 02-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 2 | 70-IG-66-0001 |  | 70-IG-66-0001 | 02-WO-0002 | Welding Socket Outlet X 2EA (02-WO-03 & 02-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 3 | 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0001 | Welding Socket Outlet X 2EA (03-WO-01 & 03-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 3 | 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0002 | Welding Socket Outlet X 2EA (03-WO-03 & 03-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 3 | 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0003 | Welding Socket Outlet X 2EA (03-WO-05 & 03-WO-06) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 4 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0001 | Welding Socket Outlet X 2EA (04-WO-01 & 04-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 4 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0002 | Welding Socket Outlet X 2EA (04-WO-03 & 04-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 4 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0003 | Welding Socket Outlet X 2EA (04-WO-05 & 04-WO-06) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 4 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0004 | Welding Socket Outlet X 2EA (04-WO-07 & 04-WO-08) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 5 | 70-IG-66-0002 |  | 70-IG-66-0002 | 05-WO-0001 | Welding Socket Outlet X 2EA (05-WO-01 & 05-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 5 | 70-IG-66-0002 |  | 70-IG-66-0002 | 05-WO-0002 | Welding Socket Outlet X 2EA (05-WO-03 & 05-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 6 | 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0001 | Welding Socket Outlet X 2EA (06-WO-01 & 06-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 6 | 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0002 | Welding Socket Outlet X 2EA (06-WO-03 & 06-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
D | EL | 6 | 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0003 | Welding Socket Outlet X 1EA (06-WO-05) | N | F | 0.4 |  | S | 43.6464 | 43.6464 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 4.5944 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
D | EL | 7 | 70-IG-66-0002 |  | 70-IG-66-0002 | 07-WO-0001 | Welding Socket Outlet X 2EA (07-WO-01 & 07-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  | Parking area (Plant entrance area) 1ea |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C | EL | 8 | 70-IG-66-0002 |  | 70-IG-66-0002 | 08-WO-0001 | Welding Socket Outlet X 2EA (08-WO-01 & 08-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added
20260120 Dry TR 추가, 용량 수정
C3 | EL | 3 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0065A | 400/230V Normal L & SP DB - ITR West-Process - Indoor A | N | L | 0.4 |  | C | 21 | 30 | 53.6239 | 0.7 | 95 | 0.85 | 100 | 22.1053 | 13.6996 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 3 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0065B | 400/230V Normal L & SP DB - ITR West-Process - Indoor B | N | L | 0.4 |  | C | 26 | 30 | 53.6239 | 0.86667 | 95 | 0.85 | 100 | 27.3684 | 16.9614 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 3 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0066 | 400/230V Normal L & SP DB - Process - Outdoor | N | L | 0.4 |  | C | 32 | 40 | 71.4985 | 0.8 | 95 | 0.85 | 100 | 33.6842 | 20.8756 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 FEED EQ LIST Added
C3 | EL | 3 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-65-0084 | 400/230V Heat Tracing - Booster and Flash Gas Compressor area - Outdoor | N | PDB | 0.4 |  | C | 40 | 85 | 129.1441 | 0.47059 | 95 | 1 | 100 | 42.1053 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 Load Type 수정
C3 | EL | 2 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-65-0085 | 400/230V Heat Tracing - Slug Catcher Vapour recovery area - Outdoor | N | PDB | 0.4 |  | C | 40 | 85 | 129.1441 | 0.47059 | 95 | 1 | 100 | 42.1053 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 Load Type 수정
C3 | EL | 5 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-66-0001 | 400V Normal Welding Outlet DB- Outdoor B | N | F | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 0 | 0 | 59.7267 | 0 |  |  |  |  | 20260120 Added_Franca
C5 | EL | 3 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0012 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor A | Em | L | 0.4 |  | C | 14.3 | 15 | 25.4713 | 0.95333 | 100 | 0.85 | 100 | 14.3 | 8.8623 | 0 | 0 | 0 | 0 |  |  |  | ITR WEST | FEED
C5 | EL | 3 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0053 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor B | Em | L | 0.4 |  | C | 23.7 | 32 | 54.3388 | 0.74062 | 100 | 0.85 | 100 | 23.7 | 14.6879 | 0 | 0 | 0 | 0 |  |  |  | ITR WEST | FEED
C3 | EL | 3 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0019 | 400/230V Emergency L & SP DB - Process - Outdoor | Em | L | 0.4 |  | C | 32 | 40 | 67.9236 | 0.8 | 100 | 0.85 | 100 | 32 | 19.8318 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 FEED EQ LIST Added
C3 | EL | 3 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0081 | 400/230V Emergency Heat Tracing DB - Booster and Flash Gas Compressor area - Outdoor | Em | PDB | 0.4 |  | C | 60 | 85 | 122.6869 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
20251216 Load Type 수정
C3 | EL | 2 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0082 | 400/230V Emergency Heat Tracing DB - Slug Catcher Vapour recovery area - Outdoor | Em | PDB | 0.4 |  | C | 60 | 85 | 122.6869 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
20251216 Load Type 수정
C3 | EL | 4 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0083 | 400/230V Emergency Heat Tracing DB - Chemical & Utilities area - Outdoor | Em | PDB | 0.4 |  | C | 60 | 85 | 122.6869 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
20251216 Load Type 수정
C4 | EL | 3 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0017 | MOV DB - CPF - Outdoor - Booster compressor | Em | PDB | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 29.7 | 20.7307 | 0 | 0 |  |  | CI Inform Rating 반영 |  | FEED
20251216 Load Type 수정
C4 | EL | 2 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0018 | MOV DB - CPF - Outdoor - Slug Catcher | Em | PDB | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 5.07 | 3.5389 | 0 | 0 |  |  | CI Inform Rating 반영 |  | FEED
20251216 Load Type 수정
D5 | EL | 9 | 81-IG-62-0001 |  | Beach Valve | 09-WO-0001 | Welding Socket Outlet X 1EA (09-WO-01) | N | F | 0.4 |  | S | 43.6464 | 43.6464 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 4.5944 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added | DELETE
20260120 Dry TR 추가, 용량 수정