## Sheet1 (hidden)
Create a technical specification for Distribution Board based on the sources. Please note that this is for Biomethanol project.
Create a technical specification for Load Shedding System based on the sources. Please note that this is for Biomethanol project.
Create a technical specification for Power Factor Correction Panel based on the sources. Please note that this is for Biomethanol project.

## HVAC_MCC
70-IK-09-0001 (CANCELLED)
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
WH-AHU-001 | A | 78.8 | 124.8344 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
WH-ACWC-001 | A | 80.52 | 127.5592 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
WH-CWP-001A | A | 4.37 | 6.9229 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
WH-CWP-001B | A | 4.37 | 6.9229 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
WH-ACCU-001 | A | 24.5 | 38.8127 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
WH-ACCU-002 | A | 24.5 | 38.8127 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
WH-EF-001 | A | 0.37 | 1.0194 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
WH-EF-002 | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
WH-EF-003 | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
WH-EDH-001 | A | 1.32 | 2.0911 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
WH-EDH-002 | A | 1.1 | 1.7426 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
WH-WWG-001 |  | 2 | 3.1684 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
WH-WWG-002 |  | 2 | 3.1684 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
WH-HD-001 |  | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
WH-HD-002 |  | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E | 0 | 0
[13 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 8E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 0 | 0
4600
600mm Module + 400mm cable alley
[7 empty] | Transformer Space | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[7 empty] | 1200 W x 1000 D | 2000 | 800 | 0 | 2800 |  | 4600 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 2 | 1 | 0 | 3
[8 empty] | 0 |  |  |  | SPARE PANEL
70-IK-09-0002
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
WS-AHU-001 | A | 132.3 | 17.0622 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
WS-AHU-002 | A | 132.3 | 17.0622 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
WS-ACWC-001 | A | 147.6 | 201.8295 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
WS-ACWC-002 | A | 147.6 | 201.8295 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
WS-CWP-001A | A | 8.81 | 12.0469 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
WS-CWP-001B | A | 8.81 | 12.0469 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
WS-CWP-002A | A | 8.81 | 12.0469 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
WS-CWP-002B | A | 8.81 | 12.0469 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
WS-ACCU-001A | A | 31.29 | 42.7862 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
WS-ACCU-001B | A | 31.29 | 42.7862 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
WS-ACCU-002A | A | 19.22 | 26.2816 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
WS-ACCU-002B | A | 19.22 | 26.2816 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
WS-EF-001 | A | 0.37 | 0.8799 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
WS-EF-002A | A | 2.1 | 2.8716 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
WS-EF-002B | A | 2.1 | 2.8716 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E | 0 | 0
WS-EF-003 | A | 0.37 | 0.50594 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 8E | 0 | 0
WS-EF-004 | A | 0.37 | 0.50594 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 0 | 0
WS-EF-006A | A | 0.4 | 0.54696 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
WS-EF-006B | A | 0.4 | 0.54696 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
WS-EF-007A | A | 0.4 | 0.54696 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
WS-EF-007B | A | 0.4 | 0.54696 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
WS-EF-008 | A | 0.4 | 0.54696 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
WS-VAV-001 | A | 0.88 | 1.2033 | F | CHECK TAG CODE: VAV | 8E/4
WS-VAV-002 | A | 1.65 | 2.2562 | F | CHECK TAG CODE: VAV | 8E/4
WS-VAV-003 | A | 1.32 | 1.805 | F | CHECK TAG CODE: VAV | 8E/4
WS-VAV-004 | A | 2.09 | 2.8579 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
WS-VAV-005 | A | 1.87 | 2.5571 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-VAV-006 | A | 9.68 | 13.2365 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-VAV-007 | A | 3.74 | 5.1141 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-VAV-008 | A | 3.63 | 4.9637 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-VAV-009 | A | 2.42 | 3.3091 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-VAV-010 | A | 11.11 | 15.1919 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-001 | A | 1.76 | 2.4066 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-002 | A | 2.2 | 3.0083 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-003 | A | 2.42 | 3.3091 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-004 | A | 4.18 | 5.7158 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-005 | A | 4.51 | 6.167 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-006 | A | 1.1 | 1.5041 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-007 | A | 1.21 | 1.6546 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-008 | A | 0.88 | 1.2033 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-CAV-009 | A | 1.87 | 2.5571 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-WWG-001 | A | 10 | 13.6741 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-WWP-001 | A | 0.3 | 0.71343 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-HD-001 | A | 1 | 2.3781 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2
WS-HD-002 | A | 1 | 2.3781 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/2 |  | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 3000 | 800 | 0 | 3800 |  | 5600 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 3 | 1 | 0 | 4
SPARE PANEL
70-IK-09-0003
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
CB-AHU-001A | A | 154.6 | 244.9162 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
CB-AHU-001B | A | 154.6 | 244.9162 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
CB-AHU-002A | A | 56.7 | 89.8237 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
CB-AHU-002B | A | 56.7 | 89.8237 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
CB-ACWC-001A | A | 211.2 | 334.5815 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 24E | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
CB-ACWC-001B | A | 211.2 | 334.5815 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
CB-ACWC-002A | A | 82.72 | 131.0444 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
CB-ACWC-002B | A | 82.72 | 131.0444 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
CB-CWP-001A | A | 11.46 | 18.1548 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
CB-CWP-001B | A | 11.46 | 18.1548 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
CB-CWP-002A | A | 4.49 | 7.113 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
CB-CWP-002B | A | 4.49 | 7.113 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
CB-ASU-001 | A | 2.7 | 4.2773 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
CB-EF-001A | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
CB-EF-001B | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E | 0 | 0
CB-EF-002A | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 8E | 0 | 0
CB-EF-002B | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 0 | 0
CB-EF-003 | A | 0.4 | 1.102 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-004A | A | 1.9 | 3.01 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-004B | A | 1.9 | 3.01 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-005A | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-005B | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EDH-001 | A | 1.54 | 2.4397 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-002 | A | 3.19 | 5.0536 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-003 | A | 6.16 | 9.7586 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-004 | A | 1.87 | 2.9624 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-005 | A | 2.53 | 4.008 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-006 | A | 2.97 | 4.7051 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-007 | A | 3.3 | 5.2278 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-008 | A | 1.87 | 2.9624 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-009 | A | 1.87 | 2.9624 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-010 | A | 4.07 | 6.4477 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-011 | A | 1.1 | 1.7426 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-012 | A | 1.21 | 1.9169 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-WWG-001 | A | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-WWP-001 | A | 0.3 | 0.82654 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-HD-001 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-HD-002 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-HD-003 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 4000 | 2400 | 0 | 6400 |  | 9400 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 4 | 3 | 0 | 7
SPARE PANEL
70-IK-09-0004
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
AB-AHU-001A | A | 26.3 | 41.6643 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
AB-AHU-001B | A | 26.3 | 41.6643 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
AB-AHU-002 | A | 64.7 | 102.4973 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
AB-ACCU-001A | A | 33.2 | 52.5952 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
AB-ACCU-001B | A | 33.2 | 52.5952 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
AB-ACWC-001 | A | 70.8 | 112.1609 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
AB-CWP-001A | A | 3.84 | 6.0833 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
AB-CWP-001B | A | 3.84 | 6.0833 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
AB-ASU-001 | A | 1.83 | 2.8991 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
AB-FCU-001A | A | 3.82 | 10.5246 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
AB-FCU-001B | A | 3.82 | 10.5246 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
AB-FCU-001C | A | 3.82 | 10.5246 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
AB-FCU-002 | A | 2.72 | 7.4939 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
AB-FCU-003A | A | 4.94 | 13.6103 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
AB-FCU-003B | A | 4.94 | 13.6103 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E | 0 | 0
AB-FCU-003C | A | 4.94 | 13.6103 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 8E | 0 | 0
AB-FCU-004A | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 0 | 0
AB-FCU-004B | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-005 | A | 3.5 | 9.6429 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-006 | A | 3.67 | 10.1113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-007A | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-007B | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-008 | A | 2.03 | 5.5929 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-009 | A | 2.3 | 6.3368 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-010A | A | 3.39 | 9.3398 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-010B | A | 3.39 | 9.3398 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-010C | A | 3.39 | 9.3398 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-011A | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-011B | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-012A | A | 3.34 | 9.2021 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-012B | A | 3.34 | 9.2021 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-013 | A | 3.42 | 9.4225 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-014 | A | 3.42 | 9.4225 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-015A | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-015B | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-016 | A | 3.94 | 10.8552 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-017 | A | 6.68 | 18.4042 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018A | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018B | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018C | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018D | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018E | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018F | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-EF-001 | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-002 | A | 0.37 | 1.0194 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-003A | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-003B | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-004A | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-004B | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EDH-001 | A | 2.42 | 3.8337 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-WWG-001 | A | 10 | 15.8419 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-WWP-001 | A | 0.3 | 0.82654 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-001 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-002 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-003 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-004 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-005 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-006 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-007 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 4000 | 800 | 0 | 4800 |  | 6600 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 4 | 1 | 0 | 5
SPARE PANEL
70-IK-09-0005
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
MSB-AHU-001A | A | 80.3 | 127.2107 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
MSB-AHU-001B | A | 80.3 | 127.2107 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
MSB-AHU-001C | A | 80.3 | 127.2107 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
MSB-ACWC-001A | A | 140.8 | 223.0543 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
MSB-ACWC-001B | A | 140.8 | 223.0543 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
MSB-ACWC-001C | A | 140.8 | 223.0543 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
MSB-CWP-001A | A | 7.64 | 12.1032 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
MSB-CWP-001B | A | 7.64 | 12.1032 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
MSB-CWP-001C | A | 7.64 | 12.1032 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
MSB-ASU-001 | A | 2.48 | 3.9288 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
MSB-EF-001A | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
MSB-EF-001B | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
MSB-EF-002A | A | 0.5 | 0.7921 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
MSB-EF-002B | A | 0.5 | 0.7921 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
MSB-EF-003A | A | 0.5 | 0.7921 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
MSB-EF-003B | A | 0.5 | 0.7921 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
MSB-EDH-001 | A | 6.05 | 9.5844 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 2000 | 2400 | 0 | 4400 |  | 7400 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 2 | 3 | 0 | 5
SPARE PANEL
70-IK-09-0006
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
ITRE-AHU-001A | A | 96.8 | 153.3499 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
ITRE-AHU-001B | A | 96.8 | 153.3499 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
ITRE-ACCU-001A | A | 154.4 | 244.5994 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
ITRE-ACCU-001B | A | 154.4 | 244.5994 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
ITRE-ASU-001 | A | 2.23 | 3.5327 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
ITRE-EF-001A | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
ITRE-EF-001B | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
ITRE-EF-002A | A | 1 | 1.5842 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
ITRE-EF-002B | A | 1 | 1.5842 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
ITRE-EF-003A | A | 0.5 | 0.7921 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
ITRE-EF-003B | A | 0.5 | 0.7921 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
ITRE-EDH-001 | A | 6.1 | 9.6636 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
ITRE-EDH-002 | A | 7.3 | 11.5646 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 2000 | 2400 | 0 | 4400 |  | 7400 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 2 | 3 | 0 | 5
SPARE PANEL
70-IK-09-0007
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
ITRW-AHU-001A | A | 83.05 | 131.5672 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
ITRW-AHU-001B | A | 83.05 | 131.5672 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
ITRW-ACCU-001A | A | 132.4 | 209.7471 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
ITRW-ACCU-001B | A | 132.4 | 209.7471 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
ITRW-ASU-001 | A | 1.98 | 3.1367 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
ITRW-EF-001A | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
ITRW-EF-001B | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
ITRW-EF-002A | A | 0.9 | 1.4258 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
ITRW-EF-002B | A | 0.9 | 1.4258 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
ITRW-EF-003A | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
ITRW-EF-003B | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
ITRW-EDH-001 | A | 4.9 | 7.7625 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
ITRW-EDH-002 | A | 5.9 | 9.3467 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 2000 | 2400 | 0 | 4400 |  | 7400 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 2 | 3 | 0 | 5
SPARE PANEL
FIRESTATION CANCELLED?
70-IK-09-0009
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
FS-AHU-001 | A | 21.6 | 34.2186 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
FS-ACCU-001 | A | 24 | 38.0206 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
FS-EF-001 | A | 0.37 | 1.0194 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
FS-EF-002 | A | 0.37 | 1.0194 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
FS-EDH-001 | A | 1.32 | 2.0911 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
FS-EDH-002 | A | 1.21 | 1.9169 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
FS-EDH-003 | A | 1.21 | 1.9169 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
FS-WWG-001 | A | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
FS-WWP-001 | A | 0.3 | 0.82654 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
FS-HD-001 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
FS-HD-002 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
[13 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
[6 empty] | 1200 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 1000 | 800 | 0 | 1800 |  | 3600 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 1 | 1 | 0 | 2
SPARE PANEL
70-IK-09-0010
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
MGH-AHU-001 | A | 21.3 | 33.7433 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
MGH-ACCU-001 | A | 26.4 | 41.8227 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
MGH-EF-001 | A | 0.37 | 1.0194 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
MGH-EF-002A | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
MGH-EF-002B | A | 0.37 | 0.58615 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
MGH-EDH-001 | A | 1.43 | 2.2654 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
MGH-EDH-002 | A | 0.44 | 0.69704 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
MGH-EDH-003 | A | 0.99 | 1.5684 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
MGH-EDH-004 | A | 0.77 | 1.2198 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
MGH-EDH-005 | A | 1.21 | 1.9169 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
MGH-EDH-006 | A | 0.77 | 1.2198 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
MGH-EDH-007 | A | 0.55 | 0.87131 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
MGH-EDH-008 | A | 0.88 | 1.3941 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
MGH-WWG-001 | A | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
MGH-WWP-001 | A | 0.3 | 0.82654 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [11 empty] | 20
MGH-HD-001 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
MGH-HD-002 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH | [6 empty] | 24
[8 empty] | 1000 | 800 | 0 | 1800 |  | 4800 | additional 600mm for clearance between the spare space and the transformer |  |  |  | 17
[8 empty] | 1 | 1 | 0 | 2
SPARE PANEL
Apply HVAC DB Type 1
70-IK-09-0011
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
MASH02-ACCU-001 | A | 4.4 | 6.9704 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
MASH02-EF-001 | A | 0.2 | 0.55102 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
MASH02-WWG-001 | A | 2 | 3.1684 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
MASH02-HD-001 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
MASH01-ACCU-001 | A | 3.1 | 4.911 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
[13 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
[13 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
[13 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
[13 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
[13 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
[13 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 1000 | 800 | 0 | 1800 |  | 3600 | additional 600mm for clearance between the spare space and the transformer
[8 empty] | 1 | 1 | 0 | 2
SPARE PANEL
70-IK-09-0003 (Combine CB and Admin)
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
CB-AHU-001A | A | 154.6 | 244.9162 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 24E | 7 | 2
CB-AHU-001B | A | 154.6 | 244.9162 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 24E | 2 | 1
CB-AHU-002A | A | 56.7 | 89.8237 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 3 | 1
CB-AHU-002B | A | 56.7 | 89.8237 | M-E1 | 400V DOL Motor Starter Cubicle | 24E | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | 21 | 5
CB-ACWC-001A | A | 211.2 | 334.5815 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | 63 | 13
CB-ACWC-001B | A | 211.2 | 334.5815 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 24E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 2 | 1
CB-ACWC-002A | A | 82.72 | 131.0444 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E
CB-ACWC-002B | A | 82.72 | 131.0444 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E
CB-CWP-001A | A | 11.46 | 18.1548 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-CWP-001B | A | 11.46 | 18.1548 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-CWP-002A | A | 4.49 | 7.113 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-CWP-002B | A | 4.49 | 7.113 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-ASU-001 | A | 2.7 | 4.2773 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EF-001A | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-001B | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-002A | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-002B | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-003 | A | 0.4 | 1.102 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-004A | A | 1.9 | 3.01 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-004B | A | 1.9 | 3.01 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-005A | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EF-005B | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
CB-EDH-001 | A | 1.54 | 2.4397 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-002 | A | 3.19 | 5.0536 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-003 | A | 6.16 | 9.7586 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-004 | A | 1.87 | 2.9624 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-005 | A | 2.53 | 4.008 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-006 | A | 2.97 | 4.7051 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-007 | A | 3.3 | 5.2278 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-008 | A | 1.87 | 2.9624 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-009 | A | 1.87 | 2.9624 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-010 | A | 4.07 | 6.4477 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-011 | A | 1.1 | 1.7426 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-EDH-012 | A | 1.21 | 1.9169 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-WWG-001 | A | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-WWP-001 | A | 0.3 | 0.82654 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-HD-001 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-HD-002 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
CB-HD-003 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-AHU-001A | A | 26.3 | 41.6643 | M-E1 | 400V DOL Motor Starter Cubicle | 24E
AB-AHU-001B | A | 26.3 | 41.6643 | M-E1 | 400V DOL Motor Starter Cubicle | 24E
AB-AHU-002 | A | 64.7 | 102.4973 | M-E1 | 400V DOL Motor Starter Cubicle | 24E
AB-ACCU-001A | A | 33.2 | 52.5952 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E
AB-ACCU-001B | A | 33.2 | 52.5952 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E
AB-ACWC-001 | A | 70.8 | 112.1609 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E
AB-CWP-001A | A | 3.84 | 6.0833 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-CWP-001B | A | 3.84 | 6.0833 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-ASU-001 | A | 1.83 | 2.8991 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-001A | A | 3.82 | 10.5246 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-001B | A | 3.82 | 10.5246 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-001C | A | 3.82 | 10.5246 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-002 | A | 2.72 | 7.4939 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-003A | A | 4.94 | 13.6103 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-003B | A | 4.94 | 13.6103 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-003C | A | 4.94 | 13.6103 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-004A | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-004B | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-005 | A | 3.5 | 9.6429 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-006 | A | 3.67 | 10.1113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-007A | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-007B | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-008 | A | 2.03 | 5.5929 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-009 | A | 2.3 | 6.3368 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-010A | A | 3.39 | 9.3398 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-010B | A | 3.39 | 9.3398 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-010C | A | 3.39 | 9.3398 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-011A | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-011B | A | 2.77 | 7.6317 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-012A | A | 3.34 | 9.2021 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-012B | A | 3.34 | 9.2021 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-013 | A | 3.42 | 9.4225 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-014 | A | 3.42 | 9.4225 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-015A | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-015B | A | 4.69 | 12.9215 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-016 | A | 3.94 | 10.8552 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-017 | A | 6.68 | 18.4042 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018A | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018B | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018C | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018D | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018E | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-FCU-018F | A | 6.06 | 16.696 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-EF-001 | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-002 | A | 0.37 | 1.0194 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-003A | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-003B | A | 0.7 | 1.1089 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-004A | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EF-004B | A | 0.4 | 0.63368 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
AB-EDH-001 | A | 2.42 | 3.8337 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-WWG-001 | A | 10 | 15.8419 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-WWP-001 | A | 0.3 | 0.82654 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-001 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-002 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-003 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-004 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-005 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-006 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
AB-HD-007 | A | 1 | 2.7551 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 7000 | 2400 | 0 | 9400
[8 empty] | 7 | 3 | 0 | 10
3

## LoadList
REF. | SWITCHGEAR | TAG No. | DESCRIPTION | BUS REF. | Feeder type | LOAD TYPE (N / Em) | DUTY Type (C, I or S) | DUTY Load Factor | Absorbed Power (kW) (HOLD-5) | EQUIP. Design RATING (kW) | POWER FACTOR | EFFCY. (%) | Column1 | REMARKS | REV. | EQPT
1 | 70-IJ-61-0001 | 70-DM-31-1003 | Export Compressor Motor No.1 via Transformer | A | VSD-HV | N | C | 1 | 7109.00 | 8000.00 | 0.97 | 97.00 | 100 |  | 03
2 | 70-IJ-61-0001 | 70-DM-31-2003 | Export Compressor Motor No. 2 via Transformer | B | VSD-HV | N | C | 1 | 7109.00 | 8000.00 | 0.97 | 97.00 | 100 |  | 03
3 | 70-IJ-61-0001 | 70-IV-61-0001A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | A | F | N | C | 1 |  |  |  | 99.00 |  |  | 01
4 | 70-IJ-61-0001 | 70-IV-61-0001B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgeard B | B | F | N | C | 1 |  |  |  | 99.00 |  |  | 01
5 | 70-IJ-61-0001 | 70-IV-61-0001C | 11/0.72kV Transformer Feeder C for 690V Emergency Switchgear C | C | F | Em | C | 1 |  |  |  | 99.00 |  |  | 01
6 | 70-IJ-61-0001 | 70-IV-61-0003A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | A | F | N | C | 1 |  |  |  | 99.00 |  |  | 01
7 | 70-IJ-61-0001 | 70-IV-61-0003B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgear B | B | F | N | C | 1 |  |  |  | 99.00 |  |  | 01
8 | 70-IJ-61-0001 | 70-IV-61-0002A | 11/0.42kV Transformer Feeder A for 400V Normal Switchgear A | A | F | N | C | 1 |  |  |  | 99.00 |  |  | 01
9 | 70-IJ-61-0001 | 70-IV-61-0002B | 11/0.42kV Transformer Feeder B for 400V Normal Switchgear B | B | F | N | C | 1 |  |  |  | 99.00 |  |  | 01
10 | 70-IJ-61-0001 | 81-IV-61-0001 | 11/0.42kV Transformer Feeder for Beach Valve Substation LV Transformer | C | F | Em | C | 1 | 100.00 | 100.00 | 0.97 | 97.00 | 100 |  | 01
11 | 70-IJ-61-0001 | 70-DM-20-0002A | Condensate Recycle Booster Pump A | A | M-HV | N | I | 0.3 | 539.00 | 600.00 | 0.85 | 95.00 | 30 |  | 03
12 | 70-IJ-61-0001 | 70-DM-20-0002B | Condensate Recycle Booster Pump B | B | M-HV | N | S | 0.1 | 539.00 | 600.00 | 0.85 | 95.00 | 10 |  | 03
13 | 70-IJ-61-0001 | 70-DM-31-1001 | Flash Gas Compressor (1st (1001) & 2nd (1002) Stage) (Parent tag - 70-KA-31-1001) | A | M-HV | N | C | 1 | 1044.00 | 1500.00 | 0.85 | 95.00 | 100 | Note - 11 | 03
14 | 70-IJ-61-0001 | 70-DM-31-2001 | Flash Gas Compressor (1st (2001) & 2nd (2002) Stage) (Parent tag - 70-KA-31-2001) | B | M-HV | N | S | 0.1 | 1044.00 | 1500.00 | 0.85 | 95.00 | 10 | Note - 11 | 03
15 | 70-IJ-61-0001 | 70-DM-01-0002 | Electric Fire Water Pump Motor | C | VSD-HV | Em | I | 0.3 | 400.30 | 560.00 | 0.85 | 95.00 | 30 | Soft starter | 03
16 | 70-IJ-61-0001 | 70-UZ-43-0002 | MEG Regeneration Package (Electric Reboiler) | A | F | N | C | 1 | 3000.00 | 3000.00 | 1.00 | 95.00 | 100 | Note - 10 | 02
1 | 70-IK-61-0001 | 70-DM-01-0004A | Electric Fire Fighting Foam Skid Pump Motor A | C | M-B1 | Em | I | 0.3 | 78.00 | 90.00 | 0.85 | 94.00 | 30 |  | 03
2 | 70-IK-61-0001 | 70-DM-01-0004B | Electric Fire Fighting Foam Skid Pump Motor B | C | M-B1 | Em | S | 0.1 | 78.00 | 90.00 | 0.85 | 94.00 | 10 |  | 03
3 | 70-IK-61-0001 | 70-HF-05-0001A | Emergency Generator auxiliaries MCC supply A | C | F | Em | C | 1 | 50.00 | 50.00 | 0.85 | 100.00 | 100 |  | 01
4 | 70-IK-61-0001 | 70-HF-05-0001B | Emergency Generator auxiliaries MCC supply B | C | F | Em | S | 0.1 | 50.00 | 50.00 | 0.85 | 100.00 | 10 |  | 01
5 | 70-IK-61-0001 | 70-GU-06-0001A | 110V DC UPS A for Main Substation | A | U | Em | S | 0.1 | 5.00 | 5.00 | 0.85 | 100.00 | 10 |  | 01
6 | 70-IK-61-0001 | 70-GU-06-0001B | 110V DC UPS B for Main Substation | C | U | Em | C | 1 | 5.00 | 5.00 | 0.85 | 100.00 | 100 |  | 01
7 | 70-IK-61-0001 | 70-GU-06-0002A | 230V AC UPS A in Main Substation for Telecomms | A | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
8 | 70-IK-61-0001 | 70-GU-06-0002B | 230V AC UPS B in Main Substation for Telecomms | C | U | Em | C | 1 | 7.27 | 10.00 | 0.85 | 100.00 | 80 |  | 02
9 | 70-IK-61-0001 | 70-GU-06-0002 | 230V UPS Feeder Maintenance Bypass for Main Substation Telecomms | B | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
10 | 70-IK-61-0001 | 70-GU-06-0003A | 230V AC UPS A in Process - ITR for Telecomms | A | U | Em | S | 0.1 | 8.45 | 10.00 | 0.85 | 100.00 | 10 |  | 02
11 | 70-IK-61-0001 | 70-GU-06-0003B | 230V AC UPS B in Process - ITR for Telecomms | C | U | Em | C | 1 | 8.45 | 10.00 | 0.85 | 100.00 | 80 |  | 02
12 | 70-IK-61-0001 | 70-GU-06-0003 | 230V UPS Feeder Maintenance Bypass for Process - ITR Telecomms | B | U | Em | S | 0.1 | 8.45 | 10.00 | 0.85 | 100.00 | 10 |  | 02
13 | 70-IK-61-0001 | 70-GU-06-0004A | 230V AC UPS A in Process - ITR for Instruments | A | U | Em | S | 0.1 | 51.97 | 60.00 | 0.85 | 100.00 | 10 |  | 02
14 | 70-IK-61-0001 | 70-GU-06-0004B | 230V AC UPS B in Process - ITR for Instruments | C | U | Em | C | 1 | 51.97 | 60.00 | 0.85 | 100.00 | 100 |  | 02
15 | 70-IK-61-0001 | 70-GU-06-0004 | 230V UPS Feeder Maintenance Bypass for Process - ITR Instruments | B | U | Em | S | 0.1 | 51.97 | 60.00 | 0.85 | 100.00 | 10 |  | 02
16 | 70-IK-61-0001 | 70-GU-06-0005A | 230V AC UPS A in Utility - ITR for Telecomms | A | U | Em | S | 0.1 | 8.45 | 10.00 | 0.85 | 100.00 | 10 |  | 02
17 | 70-IK-61-0001 | 70-GU-06-0005B | 230V AC UPS B in Utility - ITR for Telecomms | C | U | Em | C | 1 | 8.45 | 10.00 | 0.85 | 100.00 | 80 |  | 02
18 | 70-IK-61-0001 | 70-GU-06-0005 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Telecomms | B | U | Em | S | 0.1 | 8.45 | 10.00 | 0.85 | 100.00 | 10 |  | 02
19 | 70-IK-61-0001 | 70-GU-06-0006A | 230V AC UPS A in Utility - ITR for Instruments | A | U | Em | S | 0.1 | 47.16 | 50.00 | 0.85 | 100.00 | 10 |  | 02
20 | 70-IK-61-0001 | 70-GU-06-0006B | 230V AC UPS B in Utility - ITR for Instruments | C | U | Em | C | 1 | 47.16 | 50.00 | 0.85 | 100.00 | 100 |  | 02
21 | 70-IK-61-0001 | 70-GU-06-0006 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Instruments | B | U | Em | S | 0.1 | 47.16 | 50.00 | 0.85 | 100.00 | 10 |  | 02
22 | 70-IK-61-0001 | 70-GU-06-0007A | 230V AC UPS A in Control Building for Telecomms | A | U | Em | S | 0.1 | 45.28 | 60.00 | 0.85 | 100.00 | 10 |  | 02
23 | 70-IK-61-0001 | 70-GU-06-0007B | 230V AC UPS B in Control Building for Telecomms | C | U | Em | C | 1 | 45.28 | 60.00 | 0.85 | 100.00 | 80 |  | 02
24 | 70-IK-61-0001 | 70-GU-06-0007 | 230V UPS Feeder Maintenance Bypass for Control Building Telecomms | B | U | Em | S | 0.1 | 45.28 | 60.00 | 0.85 | 100.00 | 10 |  | 02
25 | 70-IK-61-0001 | 70-GU-06-0008A | 230V AC UPS A in Control Building for Instruments | A | U | Em | S | 0.1 | 57.49 | 60.00 | 0.85 | 100.00 | 10 |  | 02
26 | 70-IK-61-0001 | 70-GU-06-0008B | 230V AC UPS B in Control Building for Instruments | C | U | Em | C | 1 | 57.49 | 60.00 | 0.85 | 100.00 | 100 |  | 02
27 | 70-IK-61-0001 | 70-GU-06-0008 | 230V UPS Feeder Maintenance Bypass for Control Building Instruments | B | U | Em | S | 0.1 | 57.49 | 60.00 | 0.85 | 100.00 | 10 |  | 02
28 | 70-IK-61-0001 | 70-GU-06-0009A | 230V AC UPS A in Warehouse for Telecoms | A | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
29 | 70-IK-61-0001 | 70-GU-06-0009B | 230V AC UPS B in Warehouse for Telecoms | C | U | Em | C | 1 | 7.27 | 10.00 | 0.85 | 100.00 | 80 |  | 02
30 | 70-IK-61-0001 | 70-GU-06-0009 | 230V UPS Feeder Maintenance Bypass for Warehouse Telecoms | B | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
31 | 70-IK-61-0001 | 70-GU-06-0010A | 230V AC UPS A in Workshop for Telecoms | A | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
32 | 70-IK-61-0001 | 70-GU-06-0010B | 230V AC UPS B in Workshop for Telecoms | C | U | Em | C | 1 | 7.27 | 10.00 | 0.85 | 100.00 | 80 |  | 02
33 | 70-IK-61-0001 | 70-GU-06-0010 | 230V UPS Feeder Maintenance Bypass for Workshop Telecoms | B | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
34 | 70-IK-61-0001 | 70-GU-06-0011A | 230V AC UPS A in Adminstration Building for Telecoms | A | U | Em | S | 0.1 | 40.41 | 40.00 | 0.85 | 100.00 | 10 |  | 02
35 | 70-IK-61-0001 | 70-GU-06-0011B | 230V AC UPS B in Adminstration Building for Telecoms | C | U | Em | C | 1 | 40.41 | 40.00 | 0.85 | 100.00 | 80 |  | 02
36 | 70-IK-61-0001 | 70-GU-06-0011 | 230V UPS Feeder Maintenance Bypass for Adminstration Building Telecoms | B | U | Em | S | 0.1 | 40.41 | 40.00 | 0.85 | 100.00 | 10 |  | 02
37 | 70-IK-61-0001 | 70-GU-06-0013A | 230V AC UPS A in Fire Station for Telecoms | A | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
38 | 70-IK-61-0001 | 70-GU-06-0013B | 230V AC UPS B in Fire Station for Telecoms | C | U | Em | C | 1 | 7.27 | 10.00 | 0.85 | 100.00 | 80 |  | 02
39 | 70-IK-61-0001 | 70-GU-06-0013 | 230V UPS Feeder Maintenance Bypass for Fire Station Telecoms | B | U | Em | S | 0.1 | 7.27 | 10.00 | 0.85 | 100.00 | 10 |  | 02
40 | 70-IK-61-0001 | 70-DM-07-0001A | Air Compressor Motor A | C | M-E1 | Em | C | 1 | 284.00 | 315.00 | 0.85 | 95.00 | 100 |  | 02
41 | 70-IK-61-0001 | 70-IK-09-0001A | HVAC control panel feeder A for Warehouse | A | F | N | C | 1 | 51.76 | 63.00 | 0.95 | 100.00 | 100 |  | 02
42 | 70-IK-61-0001 | 70-IK-09-0001B | HVAC control panel feeder B for Warehouse | B | F | N | S | 0.1 | 51.76 | 63.00 | 0.95 | 100.00 | 10 |  | 02
43 | 70-IK-61-0001 | 70-IK-09-0002A | HVAC control panel feeder A for Workshop | A | F | N | C | 1 | 223.00 | 250.00 | 0.95 | 100.00 | 100 |  | 02
44 | 70-IK-61-0001 | 70-IK-09-0002B | HVAC control panel feeder B for Workshop | B | F | N | S | 0.1 | 223.00 | 250.00 | 0.95 | 100.00 | 10 |  | 02
45 | 70-IK-61-0001 | 70-IK-09-0003A | HVAC control panel feeder A for Control Building | C | F | Em | C | 1 | 158.00 | 160.00 | 0.95 | 100.00 | 50 |  | 02
46 | 70-IK-61-0001 | 70-IK-09-0003B | HVAC control panel feeder B for Control Building | A | F | Em | S | 0.1 | 158.00 | 160.00 | 0.95 | 100.00 | 10 |  | 02
47 | 70-IK-61-0001 | 70-IK-09-0004A | HVAC control panel feeder A for Adminstration Building | A | F | N | C | 1 | 80.50 | 100.00 | 0.95 | 100.00 | 100 |  | 02
48 | 70-IK-61-0001 | 70-IK-09-0004B | HVAC control panel feeder B for Adminstration Building | B | F | N | S | 0.1 | 80.50 | 100.00 | 0.95 | 100.00 | 10 |  | 02
49 | 70-IK-61-0001 | 70-IK-09-0005A | HVAC control panel feeder A for Main Substation | C | F | Em | C | 1 | 137.70 | 160.00 | 0.95 | 100.00 | 50 |  | 02
50 | 70-IK-61-0001 | 70-IK-09-0005B | HVAC control panel feeder B for Main Substation | A | F | Em | S | 0.1 | 137.70 | 160.00 | 0.95 | 100.00 | 10 |  | 02
51 | 70-IK-61-0001 | 70-IK-09-0006A | HVAC control panel feeder A for ITR East-Utilities | C | F | Em | C | 1 | 94.47 | 100.00 | 0.95 | 100.00 | 50 |  | 02
52 | 70-IK-61-0001 | 70-IK-09-0006B | HVAC control panel feeder B for ITR East-Utilities | A | F | Em | S | 0.1 | 94.47 | 100.00 | 0.95 | 100.00 | 10 |  | 02
53 | 70-IK-61-0001 | 70-IK-09-0007A | HVAC control panel feeder A for ITR West-Process | C | F | Em | C | 1 | 94.47 | 100.00 | 0.95 | 100.00 | 50 |  | 02
54 | 70-IK-61-0001 | 70-IK-09-0007B | HVAC control panel feeder B for TR West-Process | A | F | Em | S | 0.1 | 94.47 | 100.00 | 0.95 | 100.00 | 10 |  | 02
55 | 70-IK-61-0001 | 70-IK-09-0008A | HVAC control panel feeder A for Laboratory | C | F | Em | C | 1 | 37.70 | 63.00 | 0.95 | 100.00 | 50 |  | 02
56 | 70-IK-61-0001 | 70-IK-09-0008B | HVAC control panel feeder B for Laboratory | A | F | Em | S | 0.1 | 37.70 | 63.00 | 0.95 | 100.00 | 10 |  | 02
57 | 70-IK-61-0001 | 70-IK-09-0009A | HVAC control panel feeder A for Fire Station | A | F | N | C | 1 | 31.12 | 63.00 | 0.95 | 100.00 | 100 |  | 02
58 | 70-IK-61-0001 | 70-IK-09-0009B | HVAC control panel feeder B for Fire Station | B | F | N | S | 0.1 | 31.12 | 63.00 | 0.95 | 100.00 | 10 |  | 02
59 | 70-IK-61-0001 | 70-IK-09-0010A | HVAC control panel feeder A for Main Gate House | A | F | N | C | 1 | 15.50 | 63.00 | 0.95 | 100.00 | 100 |  | 02
60 | 70-IK-61-0001 | 70-IK-09-0010B | HVAC control panel feeder B for Main Gate House | B | F | N | S | 0.1 | 15.50 | 63.00 | 0.95 | 100.00 | 10 |  | 02
61 | 70-IK-61-0001 | 70-IK-09-0011A | HVAC control panel feeder A for Plant Access Security Hut | A | F | N | C | 1 | 5.20 | 63.00 | 0.95 | 100.00 | 100 |  | 02
62 | 70-IK-61-0001 | 70-IK-09-0011B | HVAC control panel feeder B for Plant Access Security Hut | B | F | N | S | 0.1 | 5.20 | 63.00 | 0.95 | 100.00 | 10 |  | 02
63 | 70-IK-61-0001 | 70-HE-36-0002A | HP Flare KO Drum Heater A | A | H | N | I | 0.3 | 272.00 | 450.00 | 1.00 | 95.00 | 30 |  | 03
64 | 70-IK-61-0001 | 70-HE-36-0002B | HP Flare KO Drum Heater B | C | H | Em | I | 0.3 | 272.00 | 450.00 | 1.00 | 95.00 | 30 |  | 03
65 | 70-IK-61-0001 | 70-DM-36-0001A | HP Flare KO Drum Pump A (Parent tag - 70-PA-36-0001A) | C | M-B1 | Em | I | 0.3 | 14.70 | 18.50 | 0.82 | 91.60 | 30 | Note - 11 | 03
66 | 70-IK-61-0001 | 70-DM-36-0001B | HP Flare KO Drum Pump B (Parent tag - 70-PA-36-0001B) | A | M-B1 | Em | S | 0.1 | 14.70 | 18.50 | 0.82 | 91.60 | 10 | Note - 11 | 03
67 | 70-IK-61-0001 | 70-DM-36-0004A | LP Flare KO Drum Pump A (Parent tag - 70-PA-36-0004A) | C | M-A1 | Em | I | 0.3 | 5.40 | 7.50 | 0.80 | 86.60 | 30 | Note - 11 | 03
68 | 70-IK-61-0001 | 70-DM-36-0004B | LP Flare KO Drum Pump B (Parent tag - 70-PA-36-0004B) | A | M-A1 | N | S | 0.1 | 5.40 | 7.50 | 0.80 | 86.60 | 10 | Note - 11 | 03
69 | 70-IK-61-0001 | 70-HE-36-0003 | LP Flare KO Drum Heater | C | H | Em | I | 0.3 | 266.00 | 320.00 | 1.00 | 95.00 | 30 |  | 03
70 | 70-IK-61-0001 | 70-IG-62-0002 | 400/230V Emergency L & SP DB - Access control building - Indoor | C | L | Em | C | 1 | 3.55 | 5.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
71 | 70-IK-61-0001 | 70-IG-62-0003 | 400/230V Emergency L & SP DB - Control Building - Indoor | C | L | Em | C | 1 | 13.00 | 15.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
72 | 70-IK-61-0001 | 70-IG-62-0004 | 400/230V Emergency L & SP DB - Warehouse - Indoor | C | L | Em | C | 1 | 12.20 | 15.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
73 | 70-IK-61-0001 | 70-IG-62-0006 | 400/230V Emergency L & SP DB - Workshop - Indoor | C | L | Em | C | 1 | 11.40 | 15.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
74 | 70-IK-61-0001 | 70-IG-62-0007 | 400/230V Emergency L & SP DB - Adminstration Building - Indoor | C | L | Em | C | 1 | 3.20 | 5.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
75 | 70-IK-61-0001 | 70-IG-62-0008 | 400/230V Emergency L & SP DB - Laboratory - Indoor | C | L | Em | C | 1 | 2.80 | 5.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
76 | 70-IK-61-0001 | 70-IG-62-0009 | 400/230V Emergency L & SP DB - Main Substation - Indoor | C | L | Em | C | 1 | 15.00 | 15.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
77 | 70-IK-61-0001 | 70-IG-62-0010 | 400/230V Emergency L & SP DB - Fire Station - Indoor | C | L | Em | C | 1 | 4.60 | 5.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
78 | 70-IK-61-0001 | 70-IG-62-0011 | 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor | C | L | Em | C | 1 | 14.10 | 15.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
79 | 70-IK-61-0001 | 70-IG-62-0012 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor | C | L | Em | C | 1 | 14.30 | 15.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
80 | 70-IK-61-0001 | 70-IG-62-0013 | 400/230V Emergency L & SP DB - Fence Outdoor | C | L | Em | C | 1 | 27.00 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
81 | 70-IK-61-0001 | 70-IG-62-0014 | 400/230V Emergency L & SP DB - Fence Outdoor | C | L | Em | C | 1 | 27.00 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
82 | 70-IK-61-0001 | 70-IG-62-0015 | 400/230V Emergency L & SP DB - Fence Outdoor | C | L | Em | C | 1 | 27.00 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
83 | 70-IK-61-0001 | 70-IG-62-0017 | MOV Distribution Board - CPF - Outdoor - Booster compressor | C | F | Em | C | 1 | 1.70 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
84 | 70-IK-61-0001 | 70-IG-62-0018 | MOV Distribution Board - CPF - Outdoor - Slug Catcher | C | F | Em | C | 1 | 1.70 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
85 | 70-IK-61-0001 | 70-IG-62-0051 | 400/230V Emergency L & SP DB - Main Substation - Indoor | C | F | Em | C | 1 | 22.50 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
86 | 70-IK-61-0001 | 70-IG-62-0052 | 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor | C | F | Em | C | 1 | 19.50 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
87 | 70-IK-61-0001 | 70-IG-62-0053 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor | C | F | Em | C | 1 | 23.70 | 32.00 | 0.85 | 100.00 | 100 | Fed via 690/420V Isolation Transformer. | 02
88 | 70-IK-61-0001 | 70-IG-65-0080 | 400/230V Emergency Heat Tracing DB - Main Substation - Indoor | C | F | Em | C | 1 | 60.00 | 85.00 | 1.00 | 100.00 | 100 | Note-9/Fed via 690/420V Isolation Transformer. | 02
89 | 70-IK-61-0001 | 70-IG-65-0081 | 400/230V Emergency Heat Tracing DB -Booster and Flash Gas Compressor area - Outdoor | C | F | Em | C | 1 | 60.00 | 85.00 | 1.00 | 100.00 | 100 | Note-9/Fed via 690/420V Isolation Transformer. | 02
90 | 70-IK-61-0001 | 70-IG-65-0082 | 400/230V Emergency Heat Tracing DB -Slug Catcher Vapour recovery area - Outdoor | C | F | Em | C | 1 | 60.00 | 85.00 | 1.00 | 100.00 | 100 | Note-9/Fed via 690/420V Isolation Transformer. | 02
91 | 70-IK-61-0001 | 70-IG-65-0083 | 400/230V Emergency Heat Tracing DB -Chemical & Utilities area - Outdoor | C | F | Em | C | 1 | 60.00 | 85.00 | 1.00 | 100.00 | 100 | Note-9/Fed via 690/420V Isolation Transformer. | 02
92 | 70-IK-61-0001 | 70-HE-36-0005A | HP Flare KO Drum B Heater A | A | H | N | I | 0.3 | 272.00 | 450.00 | 1.00 | 95.00 | 30 |  | 03
93 | 70-IK-61-0001 | 70-HE-36-0005B | HP Flare KO Drum B Heater B | C | H | Em | I | 0.3 | 272.00 | 450.00 | 1.00 | 95.00 | 30 |  | 03
3 | 70-IK-61-0003 | 70-DM-36-0003A | HP Flare Gas Recovery Package - Liquid ring compressor A | A | VSD-G2 | N | C | 1 | 324.00 | 400.00 | 0.85 | 95.00 | 100.00 | Soft starter | 03
5 | 70-IK-61-0003 | 70-DM-25-0001A | Condensate Export Pump A | A | M-E1 | N | C | 1 | 220.00 | 250.00 | 0.85 | 95.20 | 100.00 |  | 03
7 | 70-IK-61-0003 | 70-HE-70-0001A | Fuel Gas Heater A | A | H | N | C | 1 | 40.00 | 48.00 | 1.00 | 95.00 | 100.00 |  | 03
9 | 70-IK-61-0003 | 70-DM-07-0001B | Air Compressor Motor B | A | M-E1 | N | C | 1 | 284.00 | 315.00 | 0.85 | 95.00 | 100.00 |  | 02
7 | 70-IK-61-0003 | 70-DM-20-0001A | Condensate Recycle Pump A | A | M-D1 | N | C | 1 | 216.00 | 250.00 | 0.85 | 94.70 | 100.00 |  | 03
9 | 70-IK-61-0003 | 70-HE-31-1001 | 1st Stage FGC Recycle Cooler 1 Bay - Heater | A | H | N | I | 0.3 | 12.00 | 15.00 | 1.00 | 95.00 | 30.00 |  | 03
10 | 70-IK-61-0003 | 70-HE-31-1002 | 2nd Stage FGC Suction Cooler 1 Bay - Heater | A | H | N | C | 0.3 | 20.00 | 25.00 | 1.00 | 95.00 | 30.00 |  | 03
11 | 70-IK-61-0003 | 70-HE-31-2001 | 1st Stage FGC Recycle Cooler 1 Bay - Heater | A | H | N | I | 0.3 | 12.00 | 15.00 | 1.00 | 95.00 | 30.00 |  | 03
12 | 70-IK-61-0003 | 70-HE-31-2002 | 2nd Stage FGC Suction Cooler 1 Bay - Heater | A | H | N | C | 0.3 | 20.00 | 25.00 | 1.00 | 95.00 | 30.00 |  | 03
12 | 70-IK-61-0003 | 70-DM-36-0006B | LP Flare Gas Recovery Package - Liquid ring compressor B | A | VSD-G2 | N | S | 0.1 | 324.00 | 400.00 | 0.85 | 95.00 | 10.00 | Soft starter | 03
1 | 70-IK-61-0003 | 70-HF-01-0001A | Diesel Firewater Pump Miscellaneous Users A | A | F | N | S | 0.1 | 15.00 | 15.00 | 0.85 | 95.00 | 10.00 |  | 01
5 | 70-IK-61-0003 | 70-DM-01-0003A | Fire Water Jockey Pump Motor A | A | M-B1 | N | C | 1 | 41.50 | 55.00 | 0.85 | 93.50 | 100.00 |  | 03
9 | 70-IK-61-0003 | 70-DM-28-0001 | Open Drains Recovered Oil Pump | A | M-A1 | N | I | 0.3 | 20.90 | 30.00 | 0.85 | 92.30 | 30.00 |  | 02
10 | 70-IK-61-0003 | 70-DM-28-0001A | Closed Drains Drum Booster Pump A | A | M-A1 | N | I | 0.3 | 1.50 | 4.00 | 0.82 | 91.20 | 30.00 |  | 03
14 | 70-IK-61-0003 | 70-DM-28-0003A | Open Drains Treatment Oil Pump A | A | M-A1 | N | I | 0.3 | 1.46 | 4.00 | 0.80 | 86.60 | 30.00 |  | 02
16 | 70-IK-61-0003 | 70-DM-28-0004A | OffSpec Water Recycle Pump A | A | M-A1 | N | I | 0.3 | 3.15 | 5.50 | 0.80 | 88.70 | 30.00 |  | 03
21 | 70-IK-61-0003 | 70-DM-31-1003 | 1st Stage FGC Suction Scrubber Pump (Parent tag - 70-PR-31-1001) | A | M-A1 | N | I | 0.3 | 0.032 | 0.75 | 0.80 | 81.40 | 30.00 | Note - 11 | 03
23 | 70-IK-61-0003 | 70-EA-31-1011 | Export Compressor Train 1 Aftercooler Bay 1 Fan № 1 | A | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
24 | 70-IK-61-0003 | 70-EA-31-1012 | Export Compressor Train 1 Aftercooler Bay 1 Fan № 2 | A | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
25 | 70-IK-61-0003 | 70-EA-31-1021 | Export Compressor Train 1 Aftercooler Bay 1 Fan № 3 | A | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
26 | 70-IK-61-0003 | 70-EA-31-1022 | Export Compressor Train 1 Aftercooler Bay 2 Fan № 1 | A | M-B1 | N | S | 0.1 | 18.84 | 22.00 | 0.82 | 91.60 | 10.00 |  | 03
27 | 70-IK-61-0003 | 70-EA-31-1031 | Export Compressor Train 1 Aftercooler | A | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
28 | 70-IK-61-0003 | 70-EA-31-1032 | Export Compressor Train 1 Aftercooler | A | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
39 | 70-IK-61-0003 | 70-DM-31-1111 | 1st Stage FGC Recycle Cooler 1 Bay Fan № 1 | A | M-A1 | N | I | 0.3 | 2.40 | 4.00 | 0.80 | 85.50 | 30.00 |  | 03
40 | 70-IK-61-0003 | 70-DM-31-1112 | 1st Stage FGC Recycle Cooler 1 Bay Fan № 2 | A | M-A1 | N | I | 0.3 | 2.40 | 4.00 | 0.80 | 85.50 | 30.00 |  | 03
43 | 70-IK-61-0003 | 70-DM-31-1211 | 2nd Stage FGC Suction Cooler 1 Bay Fan № 1 | A | M-A1 | N | C | 1 | 2.40 | 4.00 | 0.80 | 88.70 | 100.00 |  | 03
44 | 70-IK-61-0003 | 70-DM-31-1212 | 2nd Stage FGC Suction Cooler 1 Bay Fan № 2 | A | M-A1 | N | C | 1 | 2.40 | 4.00 | 0.80 | 88.70 | 100.00 |  | 03
48 | 70-IK-61-0003 | 70-DM-43-0001A | Rich MEG Pump Motor A | A | M-A1 | N | C | 1 | 8.75 | 11.00 | 0.82 | 89.80 | 100.00 |  | 02
50 | 70-IK-61-0003 | 70-UZ-43-0002 | MEG Regeneration Package (MEG Pump Motor No.1) | A | M-A1 | N | C | 1 | 5.50 | 5.50 | 0.80 | 87.70 | 100.00 | Note - 10 | 02
52 | 70-IK-61-0003 | 70-UZ-43-0002 | MEG Regeneration Package (MEG Reflux Pump Motor No. 1) | A | M-A1 | N | C | 1 | 15.00 | 15.00 | 0.82 | 90.60 | 100.00 | Note - 10 | 02
54 | 70-IK-61-0003 | 70-UZ-43-0002 | MEG Regeneration Package (MEG Cooler/Condenser) | A | M-B1 | N | C | 1 | 50.00 | 50.00 | 0.85 | 93.50 | 100.00 | Note - 10 | 02
55 | 70-IK-61-0003 | 70-UZ-43-0002 | MEG Regeneration Package (HC Drain pump No. 1) | A | M-A1 | N | I | 0.3 | 4.00 | 4.00 | 0.80 | 86.60 | 30.00 | Note - 10 | 02
57 | 70-IK-61-0003 | 70-DM-43-0003A | Lean MEG Transfer Pump Motor A | A | M-A1 | N | C | 1 | 2.50 | 7.50 | 0.80 | 85.50 | 100.00 |  | 02
60 | 70-IK-61-0003 | 70-IG-62-0055 | 400/230V Normal L & SP DB - Access control building - Indoor | A | L | N | C | 1 | 2.10 | 5.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
61 | 70-IK-61-0003 | 70-IG-62-0056A | 400/230V Normal L & SP DB - Control Building - Indoor A | A | L | N | C | 1 | 26.50 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
63 | 70-IK-61-0003 | 70-IG-62-0057A | 400/230V Normal L & SP DB - Warehouse - Indoor A | A | L | N | C | 1 | 28.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
65 | 70-IK-61-0003 | 70-IG-62-0059A | 400/230V Normal L & SP DB - Workshop - Indoor A | A | L | N | C | 1 | 24.50 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
68 | 70-IK-61-0003 | 70-IG-62-0061 | 400/230V Normal L & SP DB - Laboratory - Indoor | A | L | N | C | 1 | 2.70 | 5.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
69 | 70-IK-61-0003 | 70-IG-62-0062A | 400/230V Normal L & SP DB - Main Substation - Indoor A | A | L | N | C | 1 | 23.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
72 | 70-IK-61-0003 | 70-IG-62-0064A | 400/230V Normal L & SP DB - ITR East-Utilities - Indoor A | A | L | N | C | 1 | 28.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
74 | 70-IK-61-0003 | 70-IG-62-0065A | 400/230V Normal L & SP DB - ITR West-Process - Indoor A | A | L | N | C | 1 | 21.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
78 | 70-IK-61-0003 | 70-DM-71-0001A | Diesel Transfer and Filtration Package Pump Motor A | A | M-A1 | N | I | 0.3 | 2.20 | 2.20 | 0.80 | 84.30 | 30.00 |  | 01
82 | 70-IK-61-0003 | 70-DM-72-0001A | Heating Medium Circulation Pump A | A | M-B1 | N | C | 1 | 79.20 | 90.00 | 0.85 | 93.50 | 100.00 |  | 02
84 | 70-IK-61-0003 | 70-HF-72-0001A | Fired Heater Auxiliaries A | A | F | N | C | 1 | 9.80 | 10.00 | 0.85 | 95.00 | 100.00 |  | 02
87 | 70-IK-61-0003 | 70-UI-75-0001 | Pour Point Depressant Injection Package | A | F | N | I | 0.3 | 0.21 | 0.75 | 0.85 | 95.00 | 30.00 |  | 02
89 | 70-IK-61-0003 | 70-UI-75-0003 | Biocide Injection Package | A | F | N | I | 0.3 | 0.05 | 0.75 | 0.85 | 95.00 | 30.00 |  | 02
1 | 70-IK-61-0002 | 70-HE-28-0001 | Closed Drains Drum Heater | B | H | N | I | 0.3 | 68.00 | 84.00 | 1.00 | 95.00 | 30.00 |  | 02
2 | 70-IK-61-0002 | 70-HE-35-0001 | Start-Up Gas Heater | B | H | N | I | 0.3 | 530.00 | 636.00 | 1.00 | 95.00 | 30.00 |  | 02
4 | 70-IK-61-0002 | 70-DM-36-0006A | LP Flare Gas Recovery Package - Liquid ring compressor A | B | VSD-G2 | N | C | 1 | 324.00 | 400.00 | 0.85 | 95.00 | 100.00 | Soft starter | 03
6 | 70-IK-61-0002 | 70-DM-25-0001B | Condensate Export Pump B | B | M-E1 | N | S | 0.1 | 220.00 | 250.00 | 0.85 | 95.20 | 10.00 |  | 03
8 | 70-IK-61-0002 | 70-HE-70-0001B | Fuel Gas Heater B | B | H | N | S | 0.1 | 40.00 | 48.00 | 1.00 | 95.00 | 10.00 |  | 03
10 | 70-IK-61-0002 | 70-DM-07-0001C | Air Compressor Motor C | B | M-E1 | N | S | 0.1 | 284.00 | 315.00 | 0.85 | 95.00 | 10.00 |  | 02
8 | 70-IK-61-0002 | 70-DM-20-0001B | Condensate Recycle Pump B | B | M-D1 | N | S | 0.1 | 216.00 | 250.00 | 0.85 | 94.70 | 10.00 |  | 03
11 | 70-IK-61-0002 | 70-DM-36-0003B | HP Flare Gas Recovery Package - Liquid ring compressor B | B | VSD-G2 | N | S | 0.1 | 324.00 | 400.00 | 0.85 | 95.00 | 10.00 | Soft starter | 03
2 | 70-IK-61-0002 | 70-HF-01-0001B | Diesel Firewater Pump Miscellaneous Users B | B | F | N | I | 0.3 | 15.00 | 15.00 | 0.85 | 95.00 | 30.00 |  | 01
3 | 70-IK-61-0002 | 70-HF-01-0001C | Diesel Firewater Pump Miscellaneous Users C | B | F | N | I | 0.3 | 15.00 | 15.00 | 0.85 | 95.00 | 30.00 |  | 02
4 | 70-IK-61-0002 | 70-HF-01-0002 | Fire water pump control panel | B | F | N | C | 1 | 3.80 | 5.00 | 0.85 | 95.00 | 100.00 |  | 02
6 | 70-IK-61-0002 | 70-DM-01-0003B | Fire Water Jockey Pump Motor B | B | M-B1 | N | S | 0.1 | 41.50 | 55.00 | 0.85 | 93.50 | 10.00 |  | 03
11 | 70-IK-61-0002 | 70-DM-28-0001B | Closed Drains Drum Booster Pump B | B | M-A1 | N | S | 0.1 | 1.50 | 4.00 | 0.82 | 91.20 | 10.00 |  | 03
15 | 70-IK-61-0002 | 70-DM-28-0003B | Open Drains Treatment Oil Pump B | B | M-A1 | N | S | 0 | 1.46 | 4.00 | 0.80 | 86.60 | 0.00 |  | 02
17 | 70-IK-61-0002 | 70-DM-28-0004B | OffSpec Water Recycle Pump B | B | M-A1 | N | S | 0.1 | 3.15 | 5.50 | 0.80 | 88.70 | 10.00 |  | 03
22 | 70-IK-61-0002 | 70-DM-31-2003 | 1st Stage FGC Suction Scrubber Pump (Parent tag - 70-PR-31-2001) | B | M-A1 | N | S | 0.1 | 0.032 | 0.75 | 0.80 | 81.40 | 10.00 | Note - 11 | 03
31 | 70-IK-61-0002 | 70-EA-31-2011 | Export Compressor Train 2 Aftercooler Bay 1 Fan № 1 | B | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
32 | 70-IK-61-0002 | 70-EA-31-2012 | Export Compressor Train 2 Aftercooler Bay 1 Fan № 2 | B | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
33 | 70-IK-61-0002 | 70-EA-31-2013 | Export Compressor Train 2 Aftercooler Bay 1 Fan № 3 | B | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
34 | 70-IK-61-0002 | 70-EA-31-2021 | Export Compressor Train 2 Aftercooler Bay 2 Fan № 1 | B | M-B1 | N | S | 0.1 | 18.84 | 22.00 | 0.82 | 91.60 | 10.00 |  | 03
35 | 70-IK-61-0002 | 70-EA-31-2022 | Export Compressor Train 2 Aftercooler | B | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
36 | 70-IK-61-0002 | 70-EA-31-2023 | Export Compressor Train 2 Aftercooler | B | M-B1 | N | C | 1 | 18.84 | 22.00 | 0.82 | 91.60 | 100.00 |  | 03
41 | 70-IK-61-0002 | 70-DM-31-1113 | 1st Stage FGC Recycle Cooler 1 Bay Fan № 3 | B | M-A1 | N | I | 0.3 | 2.40 | 4.00 | 0.80 | 85.50 | 30.00 |  | 03
45 | 70-IK-61-0002 | 70-DM-31-1213 | 2nd Stage FGC Suction Cooler 1 Bay Fan № 3 | B | M-A1 | N | S | 0.1 | 2.40 | 4.00 | 0.80 | 88.70 | 10.00 |  | 03
47 | 70-IK-61-0002 | 70-UZ-43-0001 | Subsea MEG Injection Package | B | F | N | C | 1 | 148.00 | 185.00 | 0.85 | 95.00 | 100.00 |  | 03
49 | 70-IK-61-0002 | 70-DM-43-0001B | Rich MEG Pump Motor B | B | M-A1 | N | S | 0.1 | 8.75 | 11.00 | 0.82 | 89.80 | 10.00 |  | 02
51 | 70-IK-61-0002 | 70-UZ-43-0002 | MEG Regeneration Package (MEG Pump Motor No.2) | B | M-A1 | N | S | 0.1 | 5.50 | 5.50 | 0.80 | 87.70 | 10.00 | Note - 10 | 02
53 | 70-IK-61-0002 | 70-UZ-43-0002 | MEG Regeneration Package (MEG Reflux Pump Motor No. 2) | B | M-A1 | N | S | 0.1 | 15.00 | 15.00 | 0.82 | 90.60 | 10.00 | Note - 10 | 02
56 | 70-IK-61-0002 | 70-UZ-43-0002 | MEG Regeneration Package (HC Drain pump No. 2) | B | M-A1 | N | I | 0.3 | 4.00 | 4.00 | 0.80 | 86.60 | 30.00 |  | 02
58 | 70-IK-61-0002 | 70-DM-43-0003B | Lean MEG Transfer Pump Motor B | B | M-A1 | N | S | 0.1 | 2.50 | 7.50 | 0.80 | 85.50 | 10.00 |  | 02
59 | 70-IK-61-0002 | 70-DM-43-0004 | MEG Offloading Pump Motor | B | M-A1 | N | I | 0.3 | 3.63 | 7.50 | 0.80 | 85.50 | 30.00 |  | 03
62 | 70-IK-61-0002 | 70-IG-62-0056B | 400/230V Normal L & SP DB - Control Building - Indoor B | B | L | N | C | 1 | 29.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
64 | 70-IK-61-0002 | 70-IG-62-0057B | 400/230V Normal L & SP DB - Warehouse - Indoor B | B | L | N | C | 1 | 27.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
66 | 70-IK-61-0002 | 70-IG-62-0059B | 400/230V Normal L & SP DB - Workshop - Indoor B | B | L | N | C | 1 | 26.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
67 | 70-IK-61-0002 | 70-IG-62-0060 | 400/230V Normal L & SP DB - Adminstration Building - Indoor | B | L | N | C | 1 | 1.80 | 5.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
70 | 70-IK-61-0002 | 70-IG-62-0062B | 400/230V Normal L & SP DB - Main Substation - Indoor B | B | L | N | C | 1 | 24.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
71 | 70-IK-61-0002 | 70-IG-62-0063 | 400/230V Normal L & SP DB - Fire Station - Indoor | B | L | N | C | 1 | 4.00 | 5.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
73 | 70-IK-61-0002 | 70-IG-62-0064B | 400/230V Normal L & SP DB - ITR East-Utilities - Indoor B | B | L | N | C | 1 | 25.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
75 | 70-IK-61-0002 | 70-IG-62-0065B | 400/230V Normal L & SP DB - ITR West-Process - Indoor B | B | L | N | C | 1 | 26.00 | 30.00 | 0.85 | 95.00 | 100.00 | Fed via 400/420V Isolation Transformer. | 02
76 | 70-IK-61-0002 | 70-IG-65-0084 | 400/230V Heat Tracing - Booster and Flash Gas Compressor area - Outdoor | B | F | N | C | 1 | 40.00 | 85.00 | 1.00 | 95.00 | 100.00 | Note-9 / Fed via 400/420V Isolation Transformer. | 02
77 | 70-IK-61-0002 | 70-IG-65-0085 | 400/230V Heat Tracing - Slug Catcher Vapour recovery area - Outdoor | B | F | N | C | 1 | 40.00 | 85.00 | 1.00 | 95.00 | 100.00 | Note-9 / Fed via 400/420V Isolation Transformer. | 02
79 | 70-IK-61-0002 | 70-DM-71-0001B | Diesel Transfer and Filtration Package Pump Motor B | B | M-A1 | N | S | 0.1 | 2.20 | 2.20 | 0.80 | 84.30 | 10.00 |  | 01
80 | 70-IK-61-0002 | 70-EA-72-0001 | Heating Medium Dump Cooler Fan 1 | B | M-B1 | N | I | 0.3 | 23.15 | 30.00 | 0.82 | 91.60 | 30.00 |  | 03
81 | 70-IK-61-0002 | 70-EA-72-0002 | Heating Medium Dump Cooler Fan 2 | B | M-B1 | N | S | 0.1 | 23.15 | 30.00 | 0.82 | 91.60 | 10.00 |  | 03
83 | 70-IK-61-0002 | 70-DM-72-0001B | Heating Medium Circulation Pump B | B | M-B1 | N | S | 0.1 | 79.20 | 90.00 | 0.85 | 93.50 | 10.00 |  | 02
85 | 70-IK-61-0002 | 70-HF-72-0001B | Fired Heater Auxiliaries B | B | F | N | S | 0.1 | 9.80 | 10.00 | 0.85 | 95.00 | 10.00 |  | 02
86 | 70-IK-61-0002 | 70-HF-74-0001 | Nitrogen Generation Package Auxiliaries | B | F | N | C | 1 | 0.97 | 1.00 | 0.85 | 95.00 | 100.00 |  | 02
88 | 70-IK-61-0002 | 70-UI-75-0002 | Corrosion Inhibitor Injection Package | B | F | N | C | 1 | 0.05 | 0.75 | 0.85 | 95.00 | 100.00 |  | 02
90 | 70-IK-61-0002 | 70-UI-75-0004 | Oxygen Scavenger Injection Package | B | F | N | I | 0.3 | 0.05 | 0.75 | 0.85 | 95.00 | 30.00 |  | 02
91 | 70-IK-61-0002 | 70-UZ-75-0001 | MEG injection package | B | F | N | C | 1 | 5.00 | 5.00 | 0.85 | 95.00 | 100.00 |  | 02
92 | 70-IK-61-0002 | 70-DM-85-0001A | Utility Water Pump A | A | M-A1 | N | S | 0.1 | 5.80 | 11.00 | 0.82 | 89.80 | 10.00 |  | 02
93 | 70-IK-61-0002 | 70-DM-85-0001B | Utility Water Pump B | B | M-A1 | N | C | 1 | 5.80 | 11.00 | 0.82 | 89.80 | 100.00 |  | 02
94 | 70-IK-61-0002 | 70-EA-72-0003 | Heating Medium Dump Cooler Fan 3 | A | M-B1 | N | I | 0.3 | 23.15 | 30.00 | 0.82 | 91.60 | 30.00 |  | 03
94 | 70-IK-61-0002 | 70-DM-31-2111 | 1st Stage FGC Recycle Cooler 1 Bay Fan No 1 | B | M-A1 | N | I | 0.3 | 1.20 | 4.00 | 0.80 | 85.50 | 30.00 |  | 03
95 | 70-IK-61-0002 | 70-DM-31-2112 | 1st Stage FGC Recycle Cooler 1 Bay Fan No 2 | B | M-A1 | N | I | 0.3 | 1.20 | 4.00 | 0.80 | 85.50 | 30.00 |  | 03
96 | 70-IK-61-0002 | 70-DM-31-2113 | 1st Stage FGC Recycle Cooler 1 Bay Fan No 3 | A | M-A1 | N | S | 0.1 | 1.20 | 4.00 | 0.80 | 85.50 | 10.00 |  | 03
97 | 70-IK-61-0002 | 70-DM-31-2211 | 2nd Stage FGC Suction Cooler 1 Bay Fan № 1 | B | M-A1 | N | C | 1 | 2.70 | 4.00 | 0.80 | 88.70 | 100.00 |  | 03
98 | 70-IK-61-0002 | 70-DM-31-2212 | 2nd Stage FGC Suction Cooler 1 Bay Fan № 2 | B | M-A1 | N | C | 1 | 2.70 | 4.00 | 0.80 | 88.70 | 100.00 |  | 03
99 | 70-IK-61-0002 | 70-DM-31-2213 | 2nd Stage FGC Suction Cooler 1 Bay Fan № 3 | A | M-A1 | N | S | 0.1 | 2.70 | 4.00 | 0.80 | 88.70 | 10.00 |  | 03
94 | 70-IK-61-0002 | 70-DM-28-0007A | Closed Drains Pump A | A | M-A1 | N | I | 0.3 | 11.30 | 15.00 | 0.82 | 89.80 | 30.00 |  | 03
95 | 70-IK-61-0002 | 70-DM-28-0007B | Closed Drains Pump B | B | M-A1 | N | S | 0.3 | 11.30 | 15.00 | 0.82 | 89.80 | 30.00 |  | 03
2026-02-09
| SWGR/MCC No. | Bus | SWGR/MCC No. & Bus | Equipment Tag No. | EQUIPMENT Description | Type of Service N-Normal, Em-Emergency, SA-UPS Power | Load Type | Voltage [KV]
| 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1003 Main Motor | Export Compressor _ Main Motor | N | VSD-HV | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-KA-31-2003 Main Motor | Export Compressor _ Main Motor | N | VSD-HV | 11
| 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0001A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0001B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgeard B | N | F | 11
| 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0003A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0003B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgear B | N | F | 11
| 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0002A | 11/0.42kV Transformer Feeder A for 400V Normal Switchgear A | N | F | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0002B | 11/0.42kV Transformer Feeder B for 400V Normal Switchgear B | N | F | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 81-IK-61-0001 | 11/0.42kV Dry type Transformer for 400/230 Normal L & SP DB for Beach Valve Substation (81-IG-62-0001) | N | F | 11
| 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-A-20-0002A -Main Motor | Condensate Recycle Booster Pump A | N | M-HV | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-A-20-0002B -Main Motor | Condensate Recycle Booster Pump B | N | M-HV | 11
| 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1001/1002-Main Motor | Main Motor for Flash Gas Compressor | N | M-HV | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-PA-01-0002 Panel(Main Motor Power) | Electric Firewater Pump UCP | Em | M-HV | 11
| 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-UZ-43-0002 | 11/0.72kV Transformer for MEG Regeneration Package - Electic Reboiler (2 x 100%) | N | F | 11
| 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-UZ-43-0002-SP | 11/0.72kV Transformer for MEG Regeneration Package - Electic Reboiler (2 x 100%) - Spare | N | F | 11
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-DM-01-0004A | Electric Fire Fighting Foam Skid Pump Motor A | Em | M-B1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-DM-01-0004B | Electric Fire Fighting Foam Skid Pump Motor B | Em | M-B1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HF-05-0001A | Emergency Generator auxiliaries MCC supply A | Em | PDB | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HF-05-0001B | Emergency Generator auxiliaries MCC supply B | Em | PDB | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0001A | 110V DC UPS A for Main Substation | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0001B | 110V DC UPS B for Main Substation | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0002A | 230V AC UPS A in Main Substation for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0002B | 230V AC UPS B in Main Substation for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0002 | 230V UPS Feeder Maintenance Bypass for Main Substation Telecomms | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0003A | 230V AC UPS A in Process - ITR for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0003B | 230V AC UPS B in Process - ITR for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0003 | 230V UPS Feeder Maintenance Bypass for Process - ITR Telecomms | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0004A | 230V AC UPS A in Process - ITR for Instruments | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0004B | 230V AC UPS B in Process - ITR for Instruments | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0004 | 230V UPS Feeder Maintenance Bypass for Process - ITR Instruments | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0005A | 230V AC UPS A in Utility - ITR for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0005B | 230V AC UPS B in Utility - ITR for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0005 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Telecomms | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0006A | 230V AC UPS A in Utility - ITR for Instruments | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0006B | 230V AC UPS B in Utility - ITR for Instruments | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0006 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Instruments | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0007A | 230V AC UPS A in Control Building for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0007B | 230V AC UPS B in Control Building for Telecomms | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0007 | 230V UPS Feeder Maintenance Bypass for Control Building Telecomms | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0008A | 230V AC UPS A in Control Building for Instruments | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0008B | 230V AC UPS B in Control Building for Instruments | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0008 | 230V UPS Feeder Maintenance Bypass for Control Building Instruments | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0010A | 230V AC UPS A in Workshop for Telecoms | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0010B | 230V AC UPS B in Workshop for Telecoms | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0010 | 230V UPS Feeder Maintenance Bypass for Workshop Telecoms | Em | U | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0011A | 230V AC UPS A in Adminstration Building for Telecoms | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0011B | 230V AC UPS B in Adminstration Building for Telecoms | Em | U | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0011 | 230V UPS Feeder Maintenance Bypass for Adminstration Building Telecoms | Em | U | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0003A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Control Building Incomer A | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0003B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Control Building Incomer B | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0005A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Substation Incomer A | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0005B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Substation Incomer B | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0006A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR East-Utilities Incomer A | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0006B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR East-Utilities Incomer B | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0007A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR West-Process Incomer A | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0007B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR West-Process Incomer B | Em | HVAC MCC | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-HE-36-0002A | HP Flare KO Drum Heater A | N | H2 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0002B | HP Flare KO Drum Heater B | Em | H2 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0003 | LP Flare KO Drum Heater | Em | H2 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0001 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Gate house - Indoor (70-IG-62-0001) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0002 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Access control building Security HUT 02 - Indoor (70-IG-62-0002) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0003 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Control Building - Indoor (70-IG-62-0003) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0006 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Workshop & Warehouse - Indoor (70-IG-62-0006) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0007 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Adminstration Building - Indoor (70-IG-62-0007) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0009 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Substation - Indoor A (70-IG-62-0009) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0011 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor A (70-IG-62-0011) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0013 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0013) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0014 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0014) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0015 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0015) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0051 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Substation - Indoor B (70-IG-62-0051) | Em | F | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0052 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor B (70-IG-62-0052) | Em | F | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-65-0080 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency Heat Tracing DB - Main Substation - Indoor (70-IG-65-0080) | Em | PDB | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0094 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP Main Distribution Board (70-IG-62-0094) | Em | L | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Main Motor | Main Motor for Air Compressor Package | Em | M-E1 (SS) | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-UA-07-0001B-Main Motor | Main Motor for Air Compressor Package | N | M-E1 (SS) | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-UA-07-0001C-Main Motor | Main Motor for Air Compressor Package | N | M-E1 (SS) | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Cooling Fan Motor 1 (100% x 2) | Cooling Fan Motor 1 for Air Compressor Package | Em | M-B1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Cooling Fan Motor 2 (100% x 2) | Cooling Fan Motor 2 for Air Compressor Package | Em | M-B1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Container Fan Motor 1 (100% x 2) | Container Fan Motor 1 for Air Compressor Package | Em | M-A1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Container Fan Motor 2 (100% x 2) | Container Fan Motor 2 for Air Compressor Package | Em | M-A1 | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-UA-07-0001B-Cooling Fan Motor 1 (100% x 2) | Cooling Fan Motor 1 for Air Compressor Package | N | M-B1 | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-UA-07-0001B-Cooling Fan Motor 2 (100% x 2) | Cooling Fan Motor 2 for Air Compressor Package | N | M-B1 | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-UA-07-0001B-Container Fan Motor 1 (100% x 2) | Container Fan Motor 1 for Air Compressor Package | N | M-A1 | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-UA-07-0001B-Container Fan Motor 2 (100% x 2) | Container Fan Motor 2 for Air Compressor Package | N | M-A1 | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-UA-07-0001C-Cooling Fan Motor 1 (100% x 2) | Cooling Fan Motor 1 for Air Compressor Package | N | M-B1 | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-UA-07-0001C-Cooling Fan Motor 2 (100% x 2) | Cooling Fan Motor 2 for Air Compressor Package | N | M-B1 | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-UA-07-0001C-Container Fan Motor 1 (100% x 2) | Container Fan Motor 1 for Air Compressor Package | N | M-A1 | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-UA-07-0001C-Container Fan Motor 2 (100% x 2) | Container Fan Motor 2 for Air Compressor Package | N | M-A1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0001A Motor | Motor for HP Flare KO Drum Pump | Em | M-B1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0001B Motor | Motor for HP Flare KO Drum Pump | Em | M-A1 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0004A Motor | Motor for LP Flare KO Drum Pump | Em | M-A1 | 0.69
| 70-IK-61-0001 | B | 70-IK-61-0001B | 70-PA-36-0004B Motor | Motor for LP Flare KO Drum Pump | N | M-A1 | 0.69
| 70-IK-61-0001 | A | 70-IK-61-0001A | 70-HE-36-0005A | HP Flare KO Drum B Heater A | N | H2 | 0.69
| 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0005B | HP Flare KO Drum B Heater B | Em | H2 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-HE-28-0001 | Closed Drains Drum Heater | N | H2 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-HE-35-0001 | Thyristor panel for Start up Gas Heater | N | H1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-IV-09-0002A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Workshop & Warehouse Incomer A | N | HVAC MCC | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-09-0004A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Adminstration Building Incomer A | N | HVAC MCC | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-IV-09-0010A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Gate House Incomer A | N | HVAC MCC | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-09-0011A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for HUT 02 Incomer A | N | HVAC MCC | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-DM-36-0003A | Main Motor for Liquid Ring Compressor (70-KG-36-0003A) | N | VSD-G2 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-36-0006A | Main Motor for Liquid Ring Compressor (70-KG-36-0006A) | N | VSD-G2 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-PA-25-0001A Motor | Motor for Condensate Export Pump | N | M-E1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-PA-25-0001B Motor | Motor for Condensate Export Pump | N | M-E1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-70-0001 A | Thyristor panel for Fuel Gas Heater | N | H1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-HE-70-0001 B | Thyristor panel for Fuel Gas Heater | N | H1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-PA-20-0001A Motor | Motor for Condensate Recycle Pump | N | M-E1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-PA-20-0001B Motor | Motor for Condensate Recycle Pump | N | M-E1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-31-1001 | 1st Stage FGC Recycle Cooler 1 Bay - Electric Heater | N | H2 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-31-1002 | 2nd Stage FGC Suction Cooler 1 Bay - Electric Heater | N | H2 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-DM-43-0001A | Motor for Subsea MEG Injection Package | N | M-D1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-43-0001B | Motor for Subsea MEG Injection Package | N | M-D1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-43-0001C | Motor for Subsea MEG Injection Package | N | M-D1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-36-0003B | Main Motor for Liquid Ring Compressor (70-KG-36-0003B) | N | VSD-G2 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-DM-36-0006B | Main Motor for Liquid Ring Compressor (70-KG-36-0006B) | N | VSD-G2 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-A | Export Compressor Aftercooler (Bay 1 Fan 1) | N | M-B1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-B | Export Compressor Aftercooler (Bay 1 Fan 2) | N | M-B1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-C | Export Compressor Aftercooler (Bay 1 Fan 3) | N | M-B1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-D | Export Compressor Aftercooler (Bay 2 Fan 1) | N | M-B1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-E | Export Compressor Aftercooler (Bay 2 Fan 2) | N | M-B1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-F | Export Compressor Aftercooler (Bay 2 Fan 3) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-A | Export Compressor Aftercooler (Bay 1 Fan 1) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-B | Export Compressor Aftercooler (Bay 1 Fan 2) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-C | Export Compressor Aftercooler (Bay 1 Fan 3) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-D | Export Compressor Aftercooler (Bay 2 Fan 1) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-E | Export Compressor Aftercooler (Bay 2 Fan 2) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-F | Export Compressor Aftercooler (Bay 2 Fan 3) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1001-A | 1st Stage FGC Recycle Cooler (Bay 1 Fan 1) | N | M-A1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1001-B | 1st Stage FGC Recycle Cooler (Bay 1 Fan 2) | N | M-A1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1001-C | 1st Stage FGC Recycle Cooler (Bay 1 Fan 3) | N | M-A1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1002-A | 2nd Stage FGC Suction Cooler (Bay 1 Fan 1) | N | M-A1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1002-B | 2nd Stage FGC Suction Cooler (Bay 1 Fan 2) | N | M-A1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1002-C | 2nd Stage FGC Suction Cooler (Bay 1 Fan 3) | N | M-A1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-72-0001-A | Heating Medium Dump Cooler (Bay 1 Fan 1) | N | M-B1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-72-0001-B | Heating Medium Dump Cooler (Bay 1 Fan 2) | N | M-B1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-72-0001-C | Heating Medium Dump Cooler (Bay 1 Fan 3) | N | M-B1 | 0.69
| 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A | MEG Regeneration Package - Overhead Condenser (Air cooler) | N | M-A1 | 0.69
| 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UZ-43-0002-B | MEG Regeneration Package - Lean MEG Cooler (Air cooler) | N | M-A1 | 0.69
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 Main Lube Oil Pump Motor | Export Compressor _ Main LO Pump Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 S/b Lube Oil Pump Motor | Export Compressor _ Standby LO Pump Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 LO reservoir Heater | LO Heater for Export Compressor | N | H2 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 LO Cooler Fan Motor 1 | Export Compressor _ LO cooler Fan Motor 1 | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 LO Cooler Fan Motor 2 | Export Compressor _ LO cooler Fan Motor 2 | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 LO Cooler Fan Motor 3 | Export Compressor _ LO cooler Fan Motor 3 | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 Oil Mist Eliminator Fan Motor | Export Compressor _ Oil Mist Eliminator Fan Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 VFD | Export Compressor _ VFD (Control & Fan power) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 Main Lube Oil Pump Motor | Export Compressor _ Main LO Pump Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 S/b Lube Oil Pump Motor | Export Compressor _ Standby LO Pump Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 LO reservoir Heater | LO Heater for Export Compressor | N | H2 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 LO Cooler Fan Motor 1 | Export Compressor _ LO cooler Fan Motor 1 | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 LO Cooler Fan Motor 2 | Export Compressor _ LO cooler Fan Motor 2 | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 LO Cooler Fan Motor 3 | Export Compressor _ LO cooler Fan Motor 3 | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 Oil Mist Eliminator Fan Motor | Export Compressor _ Oil Mist Eliminator Fan Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 VFD | Export Compressor _ VFD (Control & Fan power) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Aux Lube Oil Pump Motor | Aux LO Pump for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Main CW Pump Motor | Main CW Pump Motor for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Aux CW Pump Motor | Aux CW Pump Motor for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-LO Heater | LO Heater for Flash Gas Compressor | N | H2 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Coolant Heater | Coolant Heater for Flash Gas Compressor | N | H2 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Electric Barring Device Motor | Electric Barring Device Motor for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-LO Cooler Fan Motor 1 | LO Cooler Fan Motor 1 for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-LO Cooler Fan Motor 2 | LO Cooler Fan Motor 1 for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 1 | CW Console Cooler Fan Motor 1 for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 2 | CW Console Cooler Fan Motor 2 for Flash Gas Compressor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0001A Hydraulic Motor | Diesel Firewater Pump A Hydraulic Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001B Hydraulic Motor | Diesel Firewater Pump B Hydraulic Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001C Hydraulic Motor | Diesel Firewater Pump C Hydraulic Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-HF-01-0002 | Fire water pump control panel | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0003A(Main Motor Power) | Firewater Jockey Pump A UCP | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0003B(Main Motor Power) | Firewater Jockey Pump B UCP | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0001A Motor | Motor for Closed Drains Drum Booster Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0001A Seal Motor | Motor for Closed Drains Drum Booster Pump- Seal Circulation Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0001B Motor | Motor for Closed Drains Drum Booster Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0001B Seal Motor | Motor for Closed Drains Drum Booster Pump- Seal Circulation Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0004A Motor | Motor for Off spec Water Recycle Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0004B Motor | Motor for Off spec Water Recycle Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0005A Motor | Motor for Open Drains Treatment Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0005B Motor | Motor for Open Drains Treatment Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-31-1003 | 1st Stage FGC Suction Scrubber Pump Motor - Train 1 | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-43-0001A | Rich MEG Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0001B | Rich MEG Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-C | MEG Regeneration Package - Lean MEG Pump A | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-D | MEG Regeneration Package - Lean MEG Pump B | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-E | MEG Regeneration Package - Reflux Pump A | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-F | MEG Regeneration Package - Reflux Pump B | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-G | MEG Regeneration Package - Hydrocarbon Recovery Pump A | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-H | MEG Regeneration Package - Hydrocarbon Recovery Pump B | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-43-0003A | Lean MEG Transfer Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0003B | Lean MEG Transfer Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0004 | MEG Offloading Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0054 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Gate house - Indoor (70-IG-62-0054) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0055 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Access control building Security HUT 02 - Indoor (70-IG-62-0055) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0056A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building - Indoor A (70-IG-62-0056A) | N | L | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0056B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building - Indoor B (70-IG-62-0056B) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0059A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Workshop & Warehouse - Indoor A (70-IG-62-0059A) | N | L | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0059B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Workshop & Warehouse - Indoor B (70-IG-62-0059B) | N | L | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0060 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Adminstration Building - Indoor (70-IG-62-0060) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0061 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building (Laboratory room) - Indoor (70-IG-62-0061) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0062A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Substation - Indoor A (70-IG-62-0062A) | N | L | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0062B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Substation - Indoor B (70-IG-62-0062B) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0064A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - ITR East-Utilities - Indoor A (70-IG-62-0064A) | N | L | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0064B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - ITR East-Utilities - Indoor B (70-IG-62-0064B) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-66-0002 | 0.4/0.42kV Dry type Transformer for 400V Normal Welding Outlet DB- Outdoor A (70-IG-66-0002) | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0093 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP Main Distribution Board (70-IG-62-0093) | N | L | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0099 | 0.4/0.42kV Dry type Transformer for 400/230V Normal DB for EV Charging (70-IG-62-0099) | N | L | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-71-0001-A | Diesel Transfer and Filtration Package Pump Motor A | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-71-0001-B | Diesel Transfer and Filtration Package Pump Motor B | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-72-0001A | Heating Medium Circulation Pump | N | M-B1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-72-0001B | Heating Medium Circulation Pump | N | M-B1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-72--0001A (70-HF-72-0001A) | Fired Heater A FD Fan | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-72--0001B (70-HF-72-0001B) | Fired Heater B FD Fan | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UB-74-0001 Elec Heater A | Electric Heater for N2 Generation Package | N | H2 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UB-74-0001 Elec. Heater B | Electric Heater for N2 Generation Package | N | H2 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Pump A | Motor for Pour Point Depressant Injection Package | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Pump B | Motor for Pour Point Depressant Injection Package | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Agitator | Motor for Agitator | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Filling Pump | Motor for Filling Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Pump A | Motor for Corrosion Inhibitor Injection Package | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Pump B | Motor for Corrosion Inhibitor Injection Package | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Agitator | Motor for Agitator | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Filling Pump | Motor for Filling Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-75-0001-Pump A | Motor for MEG Injection Package | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-75-0001-Pump B | Motor for MEG Injection Package | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-85-0001A | Utility Water Pump A Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-85-0001B | Utility Water Pump B Motor | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-28-0007A | Closed Drains Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-28-0007B | Closed Drains Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-Liquid Ring Recirculation Pump | Motor for Liquid Ring Recirculation Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-Liquid Ring Air Cooler | Motor for Liquid Ring Air Cooler | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-LO Heater for 70-KG-36-0003A | LO Heater for Liquid Ring Compressor (70-KG-36-0003A) | N | H2 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-LO Heater for 70-KG-36-0003B | LO Heater for Liquid Ring Compressor (70-KG-36-0003B) | N | H2 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0006-Liquid Ring Recirculation Pump | Motor for Liquid Ring Recirculation Pump | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0006-Liquid Ring Air Cooler | Motor for Liquid Ring Air Cooler | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0006-LO Heater for 70-KG-36-0006A | LO Heater for Liquid Ring Compressor (70-KG-36-0006A) | N | H2 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0006-LO Heater for 70-KG-36-0006B | LO Heater for Liquid Ring Compressor (70-KG-36-0006B) | N | H2 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-85-0001_Sub item_3 | UV sterilisers includig LOP | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.1 | Aeration system(Rotor) A for IAF Unit | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.1.2 | Aeration system(Rotor) B for IAF Unit | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.3 | Aeration system(Rotor) C for IAF Unit | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.1.4 | Aeration system(Rotor) D for IAF Unit | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.5 | Skimmer for IAF Unit | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.2 | FLOAT OILY SLUDGE PUMP (included in 70-UU-28-0001) | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 3.1 | Dosing Pump_A_Demulsifying Chemical Dosing System | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 3.2 | Dosing Pump_B_Demulsifying Chemical Dosing System | N | M-A1 | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 4 | Agitator_Demulsifying Chemical Dosing System | N | M-A1 | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-JC-78-0002 | Overhead Crane - Flash Gas Compressor Shelter ( 10 Te SWL) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JC-78-0003 | Overhead Crane - Workshop Building (10 Te SWL) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JH-78-0001 | Power Hoists (various capacities) | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-JH-78-0002 | Power Hoists (various capacities) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JH-78-0003 | Power Hoists (various capacities) | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-JH-78-0004 | Power Hoists (various capacities) | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | EV-0001 (Temp) | Elevator | Em | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-CEMS-72-0001A (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (70-UZ-72-0001A) | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-CEMS-72-0001B (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (70-UZ-72-0001B) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-26-0001 | Condensate Export Metering Package (Lighting & etc.) | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0002 | SCP Export Metering Package (Lighting & etc.) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-35-0003 | DGN Export Metering Package (Lighting & etc.) | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0004 | Buy-back Gas Metering Package (Lighting & etc.) | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 82-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Production Inlet | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 83-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Gas Export | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 84-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Condensate | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 86-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - MEG | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 87-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Domestic Gas Export | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1001 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Pipelines | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1002 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Pipelines | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1011 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1012 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1013 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1014 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1003 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Pipelines | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1004 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Pipelines | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1005 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 03 Pipelines | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1006 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 03 Pipelines | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1007 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 02 Pipelines | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1008 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 02 Pipelines | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1009 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 01 Pipelines | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1010 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 01 Pipelines | N | F | 0.4
| 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1015 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Tank | N | F | 0.4
| 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1016 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Tank | N | F | 0.4
| 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 1 | EV Charging - 1 | N | F | 0.4
| 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 2 | EV Charging - 2 | N | F | 0.4
| 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 3 | EV Charging - 3 | N | F | 0.4
| 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 4 | EV Charging - 4 | N | F | 0.4
| 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 5 | EV Charging - 5 | N | F | 0.4
| 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 6 | EV Charging - 6 | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1001 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (1 of 7) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1002 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (2 of 7) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1003 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (3 of 7) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1004 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (4 of 7) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1005 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (5 of 7) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1006 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (6 of 7) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1007 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (7 of 7) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2001 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (1 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2002 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (2 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2003 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (3 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2004 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (4 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2005 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (5 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2006 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (6 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2007 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (7 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2008 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (8 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2009 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (9 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2010 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (10 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3001 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (1 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3002 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (2 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3003 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (3 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3004 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (4 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3005 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (5 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3006 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (6 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3007 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (7 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3008 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (8 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3009 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (9 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3010 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (10 of 10) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4001 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (1 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4002 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (2 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4003 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (3 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4004 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (4 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-1001 | MOV (Motor Operated Valve) for 70-UN-36-0001 Metering DBB (1 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-1002 | MOV (Motor Operated Valve) for 70-UN-36-0001 Metering DBB (2 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-1003 | MOV (Motor Operated Valve) for 70-UN-36-0001 Metering DBB (3 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-1004 | MOV (Motor Operated Valve) for 70-UN-36-0001 Metering DBB (4 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-2001 | MOV (Motor Operated Valve) for 70-UN-36-0002 Metering DBB (1 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-2002 | MOV (Motor Operated Valve) for 70-UN-36-0002 Metering DBB (2 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-2003 | MOV (Motor Operated Valve) for 70-UN-36-0002 Metering DBB (3 of 4) | N | F | 0.4
| 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-36-2004 | MOV (Motor Operated Valve) for 70-UN-36-0002 Metering DBB (4 of 4) | N | F | 0.4
| 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0001 | MOV (Motor Operated Valve) | N | F | 0.4
| 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0002 | MOV (Motor Operated Valve) | N | F | 0.4
| 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0003 | MOV (Motor Operated Valve) | N | F | 0.4
| 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0004 | MOV (Motor Operated Valve) | N | F | 0.4
| 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0005 | MOV (Motor Operated Valve) | N | F | 0.4
| 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-25-0021 | MOV (Motor Operated Valve) | N | F | 0.4
| 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-25-0022 | MOV (Motor Operated Valve) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 01-WO-0001 | Welding Socket Outlet X 2EA (01-WO-01 & 01-WO-02) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 01-WO-0002 | Welding Socket Outlet X 2EA (01-WO-03 & 01-WO-04) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 02-WO-0001 | Welding Socket Outlet X 2EA (02-WO-01 & 02-WO-02) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 02-WO-0002 | Welding Socket Outlet X 2EA (02-WO-03 & 02-WO-04) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0001 | Welding Socket Outlet X 2EA (03-WO-01 & 03-WO-02) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0002 | Welding Socket Outlet X 2EA (03-WO-03 & 03-WO-04) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0003 | Welding Socket Outlet X 2EA (03-WO-05 & 03-WO-06) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0001 | Welding Socket Outlet X 2EA (04-WO-01 & 04-WO-02) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0002 | Welding Socket Outlet X 2EA (04-WO-03 & 04-WO-04) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0003 | Welding Socket Outlet X 2EA (04-WO-05 & 04-WO-06) | N | F | 0.4
| 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0004 | Welding Socket Outlet X 2EA (04-WO-07 & 04-WO-08) | N | F | 0.4
| 70-IG-66-0002 |  | 70-IG-66-0002 | 05-WO-0001 | Welding Socket Outlet X 2EA (05-WO-01 & 05-WO-02) | N | F | 0.4
| 70-IG-66-0002 |  | 70-IG-66-0002 | 05-WO-0002 | Welding Socket Outlet X 2EA (05-WO-03 & 05-WO-04) | N | F | 0.4
| 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0001 | Welding Socket Outlet X 2EA (06-WO-01 & 06-WO-02) | N | F | 0.4
| 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0002 | Welding Socket Outlet X 2EA (06-WO-03 & 06-WO-04) | N | F | 0.4
| 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0003 | Welding Socket Outlet X 1EA (06-WO-05) | N | F | 0.4
| 70-IG-66-0002 |  | 70-IG-66-0002 | 07-WO-0001 | Welding Socket Outlet X 2EA (07-WO-01 & 07-WO-02) | N | F | 0.4
| 70-IG-66-0002 |  | 70-IG-66-0002 | 08-WO-0001 | Welding Socket Outlet X 2EA (08-WO-01 & 08-WO-02) | N | F | 0.4
| 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0065A | 400/230V Normal L & SP DB - ITR West-Process - Indoor A | N | L | 0.4
| 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0065B | 400/230V Normal L & SP DB - ITR West-Process - Indoor B | N | L | 0.4
| 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0066 | 400/230V Normal L & SP DB - Process - Outdoor | N | L | 0.4
| 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-65-0084 | 400/230V Heat Tracing - Booster and Flash Gas Compressor area - Outdoor | N | PDB | 0.4
| 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-65-0085 | 400/230V Heat Tracing - Slug Catcher Vapour recovery area - Outdoor | N | PDB | 0.4
| 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-66-0001 | 400V Normal Welding Outlet DB- Outdoor B | N | F | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0012 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor A | Em | L | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0053 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor B | Em | L | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0019 | 400/230V Emergency L & SP DB - Process - Outdoor | Em | L | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0081 | 400/230V Emergency Heat Tracing DB - Booster and Flash Gas Compressor area - Outdoor | Em | PDB | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0082 | 400/230V Emergency Heat Tracing DB - Slug Catcher Vapour recovery area - Outdoor | Em | PDB | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0083 | 400/230V Emergency Heat Tracing DB - Chemical & Utilities area - Outdoor | Em | PDB | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0017 | MOV DB - CPF - Outdoor - Booster compressor | Em | PDB | 0.4
| 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0018 | MOV DB - CPF - Outdoor - Slug Catcher | Em | PDB | 0.4
| 81-IG-62-0001 |  | 81-IG-62-0001 | 09-WO-0001 | Welding Socket Outlet X 1EA (09-WO-01) | N | F | 0.4
[7 empty] | FEEDER_CODE | VOLTAGE
[7 empty] | VSD-HV | 11
[7 empty] | F | 11
[7 empty] | M-HV | 11
[7 empty] | M-B1 | 0.69
[7 empty] | PDB | 0.69
[7 empty] | U | 0.69
[7 empty] | HVAC MCC | 0.69
[7 empty] | H2 | 0.69
[7 empty] | L | 0.69
[7 empty] | F | 0.69
[7 empty] | M-E1 (SS) | 0.69
[7 empty] | M-A1 | 0.69
[7 empty] | H1 | 0.69
[7 empty] | VSD-G2 | 0.69
[7 empty] | M-E1 | 0.69
[7 empty] | M-D1 | 0.69
[7 empty] | M-A1 | 0.4
[7 empty] | H2 | 0.4
[7 empty] | F | 0.4
[7 empty] | L | 0.4
[7 empty] | M-B1 | 0.4
[7 empty] | PDB | 0.4
Rev | Disc. | Unit | SWGR/MCC No. | Bus | SWGR/MCC No. & Bus | Equipment Tag No. | EQUIPMENT Description | Type of Service N-Normal, Em-Emergency, SA-UPS Power | Load Type | Voltage [KV] | Starter Type | Load Duty | Absorbed Power (kW) [A] | Rated Power (kW) [B] | Full Load Current | DUTY Load Factor [A/B] | Efficiency (%) [C] | Power Factor [D] | UTILIZATION (UF) (%) [E] | Consumed Load | 세로 막대형1 | 세로 막대형2 | 세로 막대형3 | 세로 막대형4 | 세로 막대형5 | Variation from FEED (Added/Deleted/Increased/ Decreased/No Change) | Variation from FEED Detail | Remarks | Location (Building) | History | 세로 막대형6
kW=(B/C)*E, kVAr=(B/C)*TAN(ACOS(D))*(F)
[20 empty] | Continuous [F] |  | Intermittent [G] |  | Standby [H]
[20 empty] | [kW] | [kVAr] | [kW] | [kVAr] | [kW] | [kVAr]
C1 | MR | 03 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1003 Main Motor | Export Compressor _ Main Motor | N | VSD-HV | 11 | VVVF | C | 10237 | 11000 | 613.6149 | 0.93064 | 97 | 0.97 | 100 | 10553.6082 | 2644.9835 | 0 | 0 | 0 | 0 | Increased | 8000KW -> 11000KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260128 IOM-ME(MR)-0010 수정
C1 | MR | 03 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-KA-31-2003 Main Motor | Export Compressor _ Main Motor | N | VSD-HV | 11 | VVVF | C | 10237 | 11000 | 613.6149 | 0.93064 | 97 | 0.97 | 100 | 10553.6082 | 2644.9835 | 0 | 0 | 0 | 0 | Increased | 8000KW -> 11000KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260128 IOM-ME(MR)-0010 수정
| EL | 05 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0001A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11 |  | C | [6 empty] | 100 | 352.315 | 115.8003 | 198.1388 | 8.6606 | 101.1244 | 43.8308 |  |  |  | MAIN SUBSTATION | FEED
D3 | EL | 05 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0001B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgeard B | N | F | 11 |  | C | [6 empty] | 100 | 1718.9095 | 798.0793 | 322.1382 | 44.4608 | 49.4269 | 31.0742 |  |  |  | MAIN SUBSTATION | FEED
| EL | 05 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0003A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11 |  | C | [6 empty] | 100 | 2073.7363 | 1061.3929 | 79.2572 | 28.3584 | 9.386 | 5.801 |  |  |  | MAIN SUBSTATION | FEED
| EL | 05 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0003B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgear B | N | F | 11 |  | C | [6 empty] | 100 | 463.4922 | 184.4036 | 70.9837 | 30.082 | 221.2006 | 90.3108 |  |  |  | MAIN SUBSTATION | FEED
| EL | 05 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0002A | 11/0.42kV Transformer Feeder A for 400V Normal Switchgear A | N | F | 11 |  | C | [6 empty] | 100 | 938.5494 | 586.87 | 49.509 | 32.7801 | 72.1303 | 8.1281 |  |  |  | MAIN SUBSTATION | FEED
| EL | 05 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0002B | 11/0.42kV Transformer Feeder B for 400V Normal Switchgear B | N | F | 11 |  | C | [6 empty] | 100 | 320.5748 | 200.2969 | 37.5451 | 24.1478 | 43.2005 | 28.3333 |  |  |  | MAIN SUBSTATION | FEED
D4 | MR | 02 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-A-20-0002A -Main Motor | Condensate Recycle Booster Pump A | N | M-HV | 11 |  | I | 539 | 720 | 46.799 | 0.74861 | 95 | 0.85 | 30 | 0 | 0 | 170.2105 | 105.487 | 0 | 0 | No Change Increased | 600KW -> 720KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 02 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-A-20-0002B -Main Motor | Condensate Recycle Booster Pump B | N | M-HV | 11 |  | S | 539 | 720 | 46.799 | 0.74861 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 56.7368 | 35.1623 | No Change Increased | 600KW -> 720KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260317 IOM-ME(MR)-0016 Rating 수정
| MR | 03 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1001/1002-Main Motor | Main Motor for Flash Gas Compressor | N | M-HV | 11 |  | C | 1044 | 1500 | 97.4979 | 0.696 | 95 | 0.85 | 100 | 1098.9474 | 681.0664 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
D3 | MR | 05 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-PA-01-0002 Panel(Main Motor Power) | Electric Firewater Pump Motor | N | M-HV | 11 |  | I | 311 | 400 | 25.9994 | 0.7775 | 95 | 0.85 | 30 | 0 | 0 | 98.2105 | 60.8654 | 0 | 0 | Decreased | 560KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 (VVVF->SS) 수정 20260130 VE SS 삭제, Normal 변경 20260225 IOM-ME(MR)-0014 Description / Rating 수정
D4 | MS | 04 | 70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-UZ-43-0002 | 11/0.72kV Transformer for MEG Regeneration Package - Electric Reboiler (2 x 100%) | N | F | 11 |  | C | 3100 | 3100 | 171.2714 | 1 | 95 | 1 | 100 | 3263.1579 | 0 | 0 | 0 | 0 | 0 | Increased | 3000KW -> 3100KW | Dedicated TR (4MVA) |  | 20250105 IOM-ME(MS)-0005 Description 수정 20260129 IOM-ME(MS)-0011 Dedicated TR 추가 20260225 IOM-ME(MS)-0026 Rating 수정 20260317 IOM-ME(MS)-0032 Description 오타 수정
D4 | MS | 04 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-UZ-43-0002-SP | 11/0.72kV Transformer for MEG Regeneration Package - Electric Reboiler (2 x 100%) - Spare | N | F | 11 |  | S | 3100 | 3100 | 171.2714 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 326.3158 | 0 | Added |  | Dedicated TR (4MVA) |  | Spare for MEG PKG Electric Heater 20260225 IOM-ME(MS)-0026 Rating 수정 20260317 IOM-ME(MS)-0032 Description 오타 수정
D3 | MS | 03 | 70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-HE-35-0001-TR | 11/0.72kV Transformer for Start up Gas Heater | N | F | 11 |  | I | 530 | 750 | 41.4366 | 0.70667 | 95 | 1 | 30 | 0 | 0 | 167.3684 | 0 | 0 | 0 | No Change |  | Dedicated TR (750kVA) |  | 20260303 추가 (TQ-720)
D | FF | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-DM-01-0004A | Electric Fire Fighting Foam Skid Pump Motor A | Em | M-B1 | 0.69 |  | I | 78 | 90 | 94.251 | 0.86667 | 94 | 0.85 | 30 | 0 | 0 | 24.8936 | 15.4277 | 0 | 0 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 기준 Deleted (FEED에만 있음) 20260206 복구함 (by FF) 20260306 consumed load 수식 복구
D | FF | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-DM-01-0004B | Electric Fire Fighting Foam Skid Pump Motor B | Em | M-B1 | 0.69 |  | S | 78 | 90 | 94.251 | 0.86667 | 94 | 0.85 | 10 | 0 | 0 | 0 | 0 | 8.2979 | 5.1426 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 기준 Deleted (FEED에만 있음) 20260206 복구함 (by FF) 20260306 consumed load 수식 복구
D | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HF-05-0001A | Emergency Generator auxiliaries MCC supply A | Em | PDB | 0.69 |  | C | 13.5 | 65 | 63.986 | 0.20769 | 100 | 0.85 | 100 | 13.5 | 8.3665 | 0 | 0 | 0 | 0 | Increased | 50KW -> 65KW |  | MAIN SUBSTATION | FEED 20251216 Load Type 수정
D | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HF-05-0001B | Emergency Generator auxiliaries MCC supply B | Em | PDB | 0.69 |  | S | 13.5 | 65 | 63.986 | 0.20769 | 100 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Increased | 50KW -> 65KW |  | MAIN SUBSTATION | FEED 20251216 Load Type 수정
| EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0001A | 110V DC UPS A for Main Substation | Em | U | 0.69 |  | S | 5 | 5 | 4.922 | 1 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.5 | 0.30987 | No Change |  |  | MAIN SUBSTATION | FEED
| EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0001B | 110V DC UPS B for Main Substation | Em | U | 0.69 |  | C | 5 | 5 | 4.922 | 1 | 100 | 0.85 | 100 | 5 | 3.0987 | 0 | 0 | 0 | 0 | No Change |  |  | MAIN SUBSTATION | FEED
D4 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0002A | 230V AC UPS A in Main Substation for Telecomms | Em | U | 0.69 |  | S | 5.35 | 10 | 9.844 | 0.535 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.535 | 0.33156 | No Change |  |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0002B | 230V AC UPS B in Main Substation for Telecomms | Em | U | 0.69 |  | C | 5.35 | 10 | 9.844 | 0.535 | 100 | 0.85 | 80 | 4.28 | 2.6525 | 0 | 0 | 0 | 0 | No Change |  |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0002 | 230V UPS Feeder Maintenance Bypass for Main Substation Telecomms | Em | U | 0.69 |  | S | 5.35 | 10 | 9.844 | 0.535 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.535 | 0.33156 | No Change |  |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0003A | 230V AC UPS A in Process - ITR for Telecomms | Em | U | 0.69 |  | S | 15.36 | 20 | 19.688 | 0.768 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.536 | 0.95193 | Increased | 10kVA -> 25kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0003B | 230V AC UPS B in Process - ITR for Telecomms | Em | U | 0.69 |  | C | 15.36 | 20 | 19.688 | 0.768 | 100 | 0.85 | 80 | 12.288 | 7.6154 | 0 | 0 | 0 | 0 | Increased | 10kVA -> 25kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0003 | 230V UPS Feeder Maintenance Bypass for Process - ITR Telecomms | Em | U | 0.69 |  | S | 15.36 | 20 | 19.688 | 0.768 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.536 | 0.95193 | Increased | 10kVA -> 25kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0004A | 230V AC UPS A in Process - ITR for Instruments | Em | U | 0.69 |  | S | 74.38 | 90 | 88.5959 | 0.82644 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 7.438 | 4.6097 | Increased | 50kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0004B | 230V AC UPS B in Process - ITR for Instruments | Em | U | 0.69 |  | C | 74.38 | 90 | 88.5959 | 0.82644 | 100 | 0.85 | 100 | 74.38 | 46.0966 | 0 | 0 | 0 | 0 | Increased | 50kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0004 | 230V UPS Feeder Maintenance Bypass for Process - ITR Instruments | Em | U | 0.69 |  | S | 74.38 | 90 | 88.5959 | 0.82644 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 7.438 | 4.6097 | Increased | 50kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0005A | 230V AC UPS A in Utility - ITR for Telecomms | Em | U | 0.69 |  | S | 8 | 10 | 9.844 | 0.8 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.8 | 0.4958 | Increased | 10kVA -> 15kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0005B | 230V AC UPS B in Utility - ITR for Telecomms | Em | U | 0.69 |  | C | 8 | 10 | 9.844 | 0.8 | 100 | 0.85 | 80 | 6.4 | 3.9664 | 0 | 0 | 0 | 0 | Increased | 10kVA -> 15kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0005 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Telecomms | Em | U | 0.69 |  | S | 8 | 10 | 9.844 | 0.8 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.8 | 0.4958 | Increased | 10kVA -> 15kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0006A | 230V AC UPS A in Utility - ITR for Instruments | Em | U | 0.69 |  | S | 64.2 | 80 | 78.752 | 0.8025 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 6.42 | 3.9788 | Increased | 50kVA -> 80kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0006B | 230V AC UPS B in Utility - ITR for Instruments | Em | U | 0.69 |  | C | 64.2 | 80 | 78.752 | 0.8025 | 100 | 0.85 | 100 | 64.2 | 39.7876 | 0 | 0 | 0 | 0 | Increased | 50kVA -> 80kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0006 | 230V UPS Feeder Maintenance Bypass for Utility - ITR Instruments | Em | U | 0.69 |  | S | 64.2 | 80 | 78.752 | 0.8025 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 6.42 | 3.9788 | Increased | 50kVA -> 80kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0007A | 230V AC UPS A in Control Building for Telecomms | Em | U | 0.69 |  | S | 51.9 | 70 | 68.908 | 0.74143 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 5.19 | 3.2165 | Increased | 60kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0007B | 230V AC UPS B in Control Building for Telecomms | Em | U | 0.69 |  | C | 51.9 | 70 | 68.908 | 0.74143 | 100 | 0.85 | 80 | 41.52 | 25.7318 | 0 | 0 | 0 | 0 | Increased | 60kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0007 | 230V UPS Feeder Maintenance Bypass for Control Building Telecomms | Em | U | 0.69 |  | S | 51.9 | 70 | 68.908 | 0.74143 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 5.19 | 3.2165 | Increased | 60kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0008A | 230V AC UPS A in Control Building for Instruments | Em | U | 0.69 |  | S | 94.79 | 130 | 127.9719 | 0.72915 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 9.479 | 5.8746 | Increased | 70kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0008B | 230V AC UPS B in Control Building for Instruments | Em | U | 0.69 |  | C | 94.79 | 130 | 127.9719 | 0.72915 | 100 | 0.85 | 100 | 94.79 | 58.7456 | 0 | 0 | 0 | 0 | Increased | 70kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D5 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0008 | 230V UPS Feeder Maintenance Bypass for Control Building Instruments | Em | U | 0.69 |  | S | 94.79 | 130 | 127.9719 | 0.72915 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 9.479 | 5.8746 | Increased | 70kVA -> 100kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0010A | 230V AC UPS A in Workshop for Telecoms | Em | U | 0.69 |  | S | 9.98 | 15 | 14.766 | 0.66533 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.998 | 0.6185 | Increased | 10kVA -> 20kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0010B | 230V AC UPS B in Workshop for Telecoms | Em | U | 0.69 |  | C | 9.98 | 15 | 14.766 | 0.66533 | 100 | 0.85 | 80 | 7.984 | 4.948 | 0 | 0 | 0 | 0 | Increased | 10kVA -> 20kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0010 | 230V UPS Feeder Maintenance Bypass for Workshop Telecoms | Em | U | 0.69 |  | S | 9.98 | 15 | 14.766 | 0.66533 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.998 | 0.6185 | Increased | 10kVA -> 20kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-GU-06-0011A | 230V AC UPS A in Adminstration Building for Telecoms | Em | U | 0.69 |  | S | 34.98 | 50 | 49.22 | 0.6996 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 3.498 | 2.1679 | Increased | 40kVA -> 60kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-GU-06-0011B | 230V AC UPS B in Adminstration Building for Telecoms | Em | U | 0.69 |  | C | 34.98 | 50 | 49.22 | 0.6996 | 100 | 0.85 | 80 | 27.984 | 17.3429 | 0 | 0 | 0 | 0 | Increased | 40kVA -> 60kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D4 | EL | 05 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-GU-06-0011 | 230V UPS Feeder Maintenance Bypass for Adminstration Building Telecoms | Em | U | 0.69 |  | S | 34.98 | 50 | 49.22 | 0.6996 | 100 | 0.85 | 10 | 0 | 0 | 0 | 0 | 3.498 | 2.1679 | Increased | 40kVA -> 60kVA |  | MAIN SUBSTATION | 20260114 UPS 수정
D | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0003A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Control Building Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 180.99 | 59.4885 | 0 | 0 | 0 | 0 |  |  |  | CONTROL BUILDING | FEED 20251216 Description / Load Type 수정
D | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0003B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Control Building Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 96.546 | 31.7331 | 16.8156 | 5.527 | 27.7203 | 9.1112 |  |  |  | CONTROL BUILDING | FEED 20251216 Description / Load Type 수정
D | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0005A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Substation Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 79.39 | 26.0942 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED 20251216 Description / Load Type 수정
D | EL | 05 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0005B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Substation Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 161.327 | 53.0256 | 2.1978 | 0.72238 | 12.0129 | 3.9484 |  |  |  | MAIN SUBSTATION | FEED 20251216 Description / Load Type 수정
D | EL | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0006A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR East-Utilities Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 84.16 | 27.6621 | 0 | 0 | 0 | 0 |  |  |  | ITR EAST | FEED 20251216 Description / Load Type 수정
D | EL | 04 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0006B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR East-Utilities Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 50.711 | 16.6679 | 4.2471 | 1.396 | 13.4871 | 4.433 |  |  |  | ITR EAST | FEED 20251216 Description / Load Type 수정
D | EL | 03 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-09-0007A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR West-Process Incomer A | Em | HVAC MCC | 0.69 |  | C | [7 empty] | 71.37 | 23.4582 | 0 | 0 | 0 | 0 |  |  |  | ITR WEST | FEED 20251216 Description / Load Type 수정
D | EL | 03 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-IV-09-0007B | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for ITR West-Process Incomer B | Em | HVAC MCC | 0.69 |  | S | [7 empty] | 43.731 | 14.3737 | 3.0888 | 1.0152 | 11.5101 | 3.7832 |  |  |  | ITR WEST | FEED 20251216 Description / Load Type 수정
C1 | MS | 01 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-HE-36-0002A | HP Flare KO Drum Heater A | N | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음) 20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 01 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0002B | HP Flare KO Drum Heater B | Em | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음) 20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 01 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0003 | LP Flare KO Drum Heater | Em | H2 | 0.69 |  | I | 266 | 320 | 281.8491 | 0.83125 | 95 | 1 | 30 | 0 | 0 | 84 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음) 20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C5 | EL | 07 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0001 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Gate house - Indoor (70-IG-62-0001) | Em | L | 0.69 |  | C | 3.55 | 5 | 4.922 | 0.71 | 100 | 0.85 | 100 | 3.55 | 2.2001 | 0 | 0 | 0 | 0 |  |  |  | MAIN GATE HOUSE | 20251216 FEED EQ LIST Added
C5 | EL | 07 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0002 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Access control building Security HUT 02 - Indoor (70-IG-62-0002) | Em | L | 0.69 |  | C | 3.55 | 5 | 4.922 | 0.71 | 100 | 0.85 | 100 | 3.55 | 2.2001 | 0 | 0 | 0 | 0 |  |  |  | SECURITY HUT 02 | FEED
C5 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0003 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Control Building - Indoor (70-IG-62-0003) | Em | L | 0.69 |  | C | 13 | 15 | 14.766 | 0.86667 | 100 | 0.85 | 100 | 13 | 8.0567 | 0 | 0 | 0 | 0 |  |  |  | CONTROL BUILDING | FEED
C5 | EL | 06 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0006 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Workshop & Warehouse - Indoor (70-IG-62-0006) | Em | L | 0.69 |  | C | 11.4 | 15 | 14.766 | 0.76 | 100 | 0.85 | 100 | 11.4 | 7.0651 | 0 | 0 | 0 | 0 |  |  |  | WORKSHOP & WAREHOUSE | FEED
C5 | EL | 06 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0007 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Adminstration Building - Indoor (70-IG-62-0007) | Em | L | 0.69 |  | C | 24 | 30 | 29.532 | 0.8 | 100 | 0.85 | 100 | 24 | 14.8739 | 0 | 0 | 0 | 0 |  |  |  | ADMINISTRATION BUILDING | FEED
C5 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0009 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Substation - Indoor A (70-IG-62-0009) | Em | L | 0.69 |  | C | 15 | 15 | 14.766 | 1 | 100 | 0.85 | 100 | 15 | 9.2962 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED
C5 | EL | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0011 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor A (70-IG-62-0011) | Em | L | 0.69 |  | C | 14.1 | 15 | 14.766 | 0.94 | 100 | 0.85 | 100 | 14.1 | 8.7384 | 0 | 0 | 0 | 0 |  |  |  | ITR EAST | FEED
C3 | EL | 00 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0013 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0013) | Em | L | 0.69 |  | C | 27 | 32 | 31.5008 | 0.84375 | 100 | 0.85 | 100 | 27 | 16.7331 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 00 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0014 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0014) | Em | L | 0.69 |  | C | 27 | 32 | 31.5008 | 0.84375 | 100 | 0.85 | 100 | 27 | 16.7331 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 00 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0015 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Fence Outdoor (70-IG-62-0015) | Em | L | 0.69 |  | C | 27 | 32 | 31.5008 | 0.84375 | 100 | 0.85 | 100 | 27 | 16.7331 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C5 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0051 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - Main Substation - Indoor B (70-IG-62-0051) | Em | F | 0.69 |  | C | 22.5 | 32 | 31.5008 | 0.70312 | 100 | 0.85 | 100 | 22.5 | 13.9442 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED
C5 | EL | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0052 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP DB - ITR East-Utilities - Indoor B (70-IG-62-0052) | Em | F | 0.69 |  | C | 19.5 | 32 | 31.5008 | 0.60938 | 100 | 0.85 | 100 | 19.5 | 12.085 | 0 | 0 | 0 | 0 |  |  |  | ITR EAST | FEED
C5 | EL | 05 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-65-0080 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency Heat Tracing DB - Main Substation - Indoor (70-IG-65-0080) | Em | PDB | 0.69 |  | C | 60 | 85 | 71.1229 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  | MAIN SUBSTATION | FEED 20251216 Load Type 수정
C3 | EL | 03 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-IV-62-0094 | 0.69/0.42kV Dry type Transformer for 400/230V Emergency L & SP Main Distribution Board (70-IG-62-0094) | Em | L | 0.69 |  | C | [6 empty] | 100 | 250 | 43.3821 | 34.77 | 24.2696 | 0 | 0 |  |  |  | ITR West | 20260203 MDB 추가
C1 | MR | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Main Motor | Main Motor for Air Compressor Package | Em | M-E1 (SS) | 0.69 | SS | C | 380 | 400 | 414.484 | 0.95 | 95 | 0.85 | 100 | 400 | 247.8977 | 0 | 0 | 0 | 0 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400) 20250105 IOM-ME(MR)-0007 수정 (400->690) 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260109 Bus 수정 20260128 IOM-ME(MR)-0010 Rating 수정
D3 | MR | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Cooling Fan Motor 1 | Cooling Fan Motor 1 for Air Compressor Package | Em | M-B1 | 0.69 |  | C | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 100 | 30.0668 | 20.9868 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260105 IOM-ME(MR)-0007 Tag, Rating 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Cooling Fan Motor 2 | Cooling Fan Motor 2 for Air Compressor Package | Em | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260105 IOM-ME(MR)-0007 Tag, Rating 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260128 IOM-ME(MR)-0010 duty 수정 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-UA-07-0001A-Container Fan Motor 1 | Container Fan Motor 1 for Air Compressor Package | Em | M-A1 | 0.69 |  | C | 2.7 | 3 | 3.409 | 0.9 | 89.8 | 0.82 | 100 | 3.0067 | 2.0987 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260225 IOM-ME(MR)-0014 Description 수정
B4 | MR | 01 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0001A Motor | Motor for HP Flare KO Drum Pump | Em | M-B1 | 0.69 |  | I | 14.7 | 18.5 | 20.6088 | 0.79459 | 91.6 | 0.82 | 30 | 0 | 0 | 4.8144 | 3.3605 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400) 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260109 Bus 수정
B4 | MR | 01 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0001B Motor | Motor for HP Flare KO Drum Pump | Em | M-A1 | 0.69 |  | S | 14.7 | 18.5 | 20.6088 | 0.79459 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.6048 | 1.1202 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400) 20251216 Load Type 수정 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260109 Bus 수정
B4 | MR | 01 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-PA-36-0004A Motor | Motor for LP Flare KO Drum Pump | Em | M-A1 | 0.69 |  | I | 5.4 | 11 | 13.2854 | 0.49091 | 86.6 | 0.8 | 30 | 0 | 0 | 1.8707 | 1.403 | 0 | 0 | Increased | 7.5KW -> 11KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400) 20251216 Load Type 수정 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260109 Bus 수정
B4 | MR | 01 | 70-IK-61-0001 | B | 70-IK-61-0001B | 70-PA-36-0004B Motor | Motor for LP Flare KO Drum Pump | N | M-A1 | 0.69 |  | S | 5.4 | 11 | 13.2854 | 0.49091 | 86.6 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.62356 | 0.46767 | Increased | 7.5KW -> 11KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400) 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
C1 | MS | 01 | 70-IK-61-0001 | A | 70-IK-61-0001A | 70-HE-36-0005A | HP Flare KO Drum B Heater A | N | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음) 20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 01 | 70-IK-61-0001 | C | 70-IK-61-0001C | 70-HE-36-0005B | HP Flare KO Drum B Heater B | Em | H2 | 0.69 |  | I | 272 | 450 | 396.3503 | 0.60444 | 95 | 1 | 30 | 0 | 0 | 85.8947 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음) 20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
C1 | MS | 01 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-HE-28-0001 | Closed Drains Drum Heater | N | H2 | 0.69 |  | I | 68 | 84 | 73.9854 | 0.80952 | 95 | 1 | 30 | 0 | 0 | 21.4737 | 0 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 기준 Deleted (FEED에만 있음) 20260129 IOM-ME(MS)-0011 추가 (FEED 기준)
D1 | MR | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001B-Main Motor | Main Motor for Air Compressor Package | N | M-E1 (SS) | 0.69 | SS | C | 380 | 400 | 414.484 | 0.95 | 95 | 0.85 | 100 | 400 | 247.8977 | 0 | 0 | 0 | 0 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400) 20250105 IOM-ME(MR)-0007 수정 (400->690) 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260128 IOM-ME(MR)-0010 Rating 수정
D1 | MR | 04 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UA-07-0001C-Main Motor | Main Motor for Air Compressor Package | N | M-E1 (SS) | 0.69 | SS | S | 380 | 400 | 414.484 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 40 | 24.7898 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (690->400) 20250105 IOM-ME(MR)-0007 수정 (400->690) 20260128 IOM-ME(MR)-0010 Rating 수정
D3 | MR | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001B-Cooling Fan Motor 1 | Cooling Fan Motor 1 for Air Compressor Package | N | M-B1 | 0.69 |  | C | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 100 | 30.0668 | 20.9868 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260105 IOM-ME(MR)-0007 Tag, Rating 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UA-07-0001B-Cooling Fan Motor 2 | Cooling Fan Motor 2 for Air Compressor Package | N | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260105 IOM-ME(MR)-0007 Tag, Rating 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260128 IOM-ME(MR)-0010 duty 수정 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001B-Container Fan Motor 1 | Container Fan Motor 1 for Air Compressor Package | N | M-A1 | 0.69 |  | C | 2.7 | 3 | 3.409 | 0.9 | 89.8 | 0.82 | 100 | 3.0067 | 2.0987 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001C-Cooling Fan Motor 1 | Cooling Fan Motor 1 for Air Compressor Package | N | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260105 IOM-ME(MR)-0007 Tag, Rating 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260128 IOM-ME(MR)-0010 duty 수정 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UA-07-0001C-Cooling Fan Motor 2 | Cooling Fan Motor 2 for Air Compressor Package | N | M-B1 | 0.69 |  | S | 27 | 30 | 34.0896 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.0067 | 2.0987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260105 IOM-ME(MR)-0007 Tag, Rating 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260128 IOM-ME(MR)-0010 duty 수정 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UA-07-0001C-Container Fan Motor 1 | Container Fan Motor 1 for Air Compressor Package | N | M-A1 | 0.69 |  | S | 2.7 | 3 | 3.409 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.30067 | 0.20987 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007 20260128 IOM-ME(MR)-0010 duty 수정 20260225 IOM-ME(MR)-0014 Description 수정
D3 | EL | 06 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-09-0004A | 0.4/0.42kV Dry type Transformer for 400/230 HVAC MCC for Adminstration Building Incomer A | N | HVAC MCC | 0.69 |  | C |  |  | #DIV/0! |  |  |  | 100 | 193.925 | 63.7401 | 4.752 | 1.5619 | 1.9796 | 0.65066 |  |  | Moved from 70-IK-61-0003 | ADMINISTRATION BUILDING | FEED 20251216 Description / Load Type 수정
D2 | EL | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-62-0093 | 0.69/0.42kV Dry type Transformer for 400/230V Normal L & SP Main Distribution Board (70-IG-62-0093) | N | L | 0.69 |  | C |  |  | #DIV/0! |  |  |  | 100 | 167.3684 | 51.5366 | 0 | 0 | 59.7267 | 0 |  |  | Moved from 70-IK-61-0002 | ITR West | 20260203 MDB 추가
D5 | EL | 06 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-IV-09-0002A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Workshop & Warehouse Incomer A | N | HVAC MCC | 0.69 |  | C | [6 empty] | 100 | 399.041 | 131.1584 | 59.2893 | 19.4875 | 1.6146 | 0.53069 |  |  | Moved to 70-IK-61-0002 | WORKSHOP & WAREHOUSE | FEED 20251216 Description / Load Type 수정
D5 | EL | 07 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-IV-09-0010A | 0.69/0.42kV Dry type Transformer for 400/230 HVAC MCC for Main Gate House Incomer A | N | HVAC MCC | 0.69 |  | C | 0 | 0 |  |  |  |  | 100 | 38.489 | 12.6507 | 6.7743 | 2.2266 | 0.0666 | 0.02189 |  |  | Moved to 70-IK-61-0002 | MAIN GATE HOUSE | FEED 20251216 Description / Load Type 수정
D5 | EL | 07 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-IV-09-0011A | 0.40/0.42kV Dry type Transformer for 400/230 HVAC MCC for HUT 02 Incomer A | N | HVAC MCC | 0.69 |  | C | 0 | 0 |  |  |  |  | 100 | 7.884 | 2.5913 | 0.81 | 0.26623 | 0 | 0 |  |  | Moved to 70-IK-61-0002 | SECURITY HUT 02 | FEED 20251216 Description / Load Type 수정
C1 | MR | 01 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-DM-36-0003A | Main Motor for Liquid Ring Compressor (70-KG-36-0003A) | N | VSD-G2 | 0.69 | VVVF | C | 320 | 355 | 367.8545 | 0.90141 | 95 | 0.85 | 100 | 336.8421 | 208.756 | 0 | 0 | 0 | 0 | Decreased | 400KW -> 355KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 (VVVF->SS) 수정 20260128 IOM-ME(MR)-0010 (SS->VVVF) 수정
B2 | MR | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-PA-25-0001A Motor | Motor for Condensate Export Pump | N | M-E1 | 0.69 |  | C | 221 | 250 | 258.5083 | 0.884 | 95.2 | 0.85 | 100 | 232.1429 | 143.8692 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating 수정 20260108 IOM-ECI(EL)-0007 CPR 답변 반영
B4 | MR | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-PA-25-0001B Motor | Motor for Condensate Export Pump | N | M-E1 | 0.69 |  | S | 221 | 250 | 258.5083 | 0.884 | 95.2 | 0.85 | 10 | 0 | 0 | 0 | 0 | 23.2143 | 14.3869 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating 수정 20260108 IOM-ECI(EL)-0007 CPR 답변 반영 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007
D4 | MS | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-70-0001A-TH | Thyristor panel for Fuel Gas Heater | N | H1 | 0.69 |  | C | 153.1 | 184 | 162.0632 | 0.83207 | 95 | 1 | 100 | 161.1579 | 0 | 0 | 0 | 0 | 0 | Increased | 48KW -> 184KW |  |  | 20251216 Load Type 수정 20250105 IOM-ME(MS)-0005 Tag/Description 수정 20260211 VE-PR-044
D4 | MS | 04 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-HE-70-0001B-TH | Thyristor panel for Fuel Gas Heater | N | H1 | 0.69 |  | S | 153.1 | 184 | 162.0632 | 0.83207 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 16.1158 | 0 | Increased | 48KW -> 184KW |  |  | 20251216 Load Type 수정 20250105 IOM-ME(MS)-0005 Tag/Description 수정 20260211 VE-PR-044
C1 | MR | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-PA-20-0001A Motor | Motor for Condensate Recycle Pump | N | M-E1 | 0.69 |  | C | 219 | 250 | 259.8731 | 0.876 | 94.7 | 0.85 | 100 | 231.2566 | 143.32 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정 20260105 IOM-ME(MR)-0007 Rating 수정 20260129 IOM-ECI(EL)-0016 Duty 수정 (CPR)
B | MR | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-PA-20-0001B Motor | Motor for Condensate Recycle Pump | N | M-E1 | 0.69 |  | S | 219 | 250 | 259.8731 | 0.876 | 94.7 | 0.85 | 10 | 0 | 0 | 0 | 0 | 23.1257 | 14.332 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정 20260105 IOM-ME(MR)-0007 Rating 수정
B | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-31-1001 | 1st Stage FGC Recycle Cooler 1 Bay - Electric Heater | N | H2 | 0.69 |  | I | 12 | 15 | 13.2117 | 0.8 | 95 | 1 | 30 | 0 | 0 | 3.7895 | 0 | 0 | 0 | No Change |  |  |  | 20251216 Load Type 수정 20250105 IOM-ME(MS)-0005 Description 수정
B | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-HE-31-1002 | 2nd Stage FGC Suction Cooler 1 Bay - Electric Heater | N | H2 | 0.69 |  | C | 28 | 35 | 30.8272 | 0.8 | 95 | 1 | 30 | 8.8421 | 0 | 0 | 0 | 0 | 0 | Increased | 15KW -> 25KW |  |  | 20251216 Load Type 수정 20250105 IOM-ME(MS)-0005 Description 수정
D4 | MR | 02 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-DM-43-0001A | Motor for Subsea MEG Injection Package | N | VSD-G2 | 0.69 |  | C | 104.5 | 110 | 113.9831 | 0.95 | 95 | 0.85 | 100 | 110 | 68.1719 | 0 | 0 | 0 | 0 | Decreased | 185KW -> 110KW |  |  | 20251202 IOM-ME(MR)-0003 수정 (400->690) 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 Rating 수정 20260317 IOM-ME(MR)-0016 VSD 반영
D4 | MR | 02 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-43-0001B | Motor for Subsea MEG Injection Package | N | VSD-G2 | 0.69 |  | I | 104.5 | 110 | 113.9831 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 33 | 20.4516 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 Rating 수정 20260317 IOM-ME(MR)-0016 VSD 반영
D4 | MR | 02 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-43-0001C | Motor for Subsea MEG Injection Package | N | VSD-G2 | 0.69 |  | S | 104.5 | 110 | 113.9831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 11 | 6.8172 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 Rating 수정 20260317 IOM-ME(MR)-0016 VSD 반영
C1 | MR | 01 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-DM-36-0003B | Main Motor for Liquid Ring Compressor (70-KG-36-0003B) | N | VSD-G2 | 0.69 | VVVF | S | 320 | 355 | 367.8545 | 0.90141 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 33.6842 | 20.8756 | Increased | 315KW -> 400KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 (VVVF->SS) 수정 20260128 IOM-ME(MR)-0010 (SS->VVVF) 수정
D4 | MS | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UB-74-0001A-TH | Thyristor Panel for Electric Heater for N2 Generation Package | N | H2 | 0.69 |  | C | 20 | 25 | 25.9052 | 0.8 | 95 | 0.85 | 100 | 21.0526 | 13.0472 | 0 | 0 | 0 | 0 | Added |  |  |  | 20250105 IOM-ME(MS)-0005 Added 20260225 IOM-ME(MS)-0026 Voltage 수정 (400 -> 690)
D4 | MS | 04 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-UB-74-0001B-TH | Thyristor Panel for Electric Heater for N2 Generation Package | N | H2 | 0.69 |  | S | 20 | 25 | 25.9052 | 0.8 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.1053 | 1.3047 | Added |  |  |  | 20250105 IOM-ME(MS)-0005 Added 20260129 IOM-ME(MS)-0011 Duty 수정 20260225 IOM-ME(MS)-0026 Voltage 수정 (400 -> 690)
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-A | Export Compressor Aftercooler (Bay 1 Fan 1) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-B | Export Compressor Aftercooler (Bay 1 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-C | Export Compressor Aftercooler (Bay 1 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-D | Export Compressor Aftercooler (Bay 2 Fan 1) | N | M-B1 | 0.69 |  | S | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.6157 | 1.1278 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-E | Export Compressor Aftercooler (Bay 2 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1004-F | Export Compressor Aftercooler (Bay 2 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-A | Export Compressor Aftercooler (Bay 1 Fan 1) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-B | Export Compressor Aftercooler (Bay 1 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-C | Export Compressor Aftercooler (Bay 1 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-D | Export Compressor Aftercooler (Bay 2 Fan 1) | N | M-B1 | 0.69 |  | S | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.6157 | 1.1278 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-E | Export Compressor Aftercooler (Bay 2 Fan 2) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-2004-F | Export Compressor Aftercooler (Bay 2 Fan 3) | N | M-B1 | 0.69 |  | C | 14.8 | 18.5 | 20.6088 | 0.8 | 91.6 | 0.82 | 100 | 16.1572 | 11.2778 | 0 | 0 | 0 | 0 | Decreased | 22KW -> 18.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1001-A | 1st Stage FGC Recycle Cooler (Bay 1 Fan 1) | N | M-A1 | 0.69 |  | I | 4.4 | 5.5 | 6.7282 | 0.8 | 85.5 | 0.8 | 30 | 0 | 0 | 1.5439 | 1.1579 | 0 | 0 | Increased | 4KW -> 5.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1001-B | 1st Stage FGC Recycle Cooler (Bay 1 Fan 2) | N | M-A1 | 0.69 |  | I | 4.4 | 5.5 | 6.7282 | 0.8 | 85.5 | 0.8 | 30 | 0 | 0 | 1.5439 | 1.1579 | 0 | 0 | Increased | 4KW -> 5.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1001-C | 1st Stage FGC Recycle Cooler (Bay 1 Fan 3) | N | M-A1 | 0.69 |  | I | 4.4 | 5.5 | 6.7282 | 0.8 | 85.5 | 0.8 | 30 | 0 | 0 | 1.5439 | 1.1579 | 0 | 0 | Increased | 4KW -> 5.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1002-A | 2nd Stage FGC Suction Cooler (Bay 1 Fan 1) | N | M-A1 | 0.69 |  | C | 6 | 7.5 | 8.8438 | 0.8 | 88.7 | 0.8 | 100 | 6.7644 | 5.0733 | 0 | 0 | 0 | 0 | Increased | 4KW -> 7.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-31-1002-B | 2nd Stage FGC Suction Cooler (Bay 1 Fan 2) | N | M-A1 | 0.69 |  | C | 6 | 7.5 | 8.8438 | 0.8 | 88.7 | 0.8 | 100 | 6.7644 | 5.0733 | 0 | 0 | 0 | 0 | Increased | 4KW -> 7.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 03 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-31-1002-C | 2nd Stage FGC Suction Cooler (Bay 1 Fan 3) | N | M-A1 | 0.69 |  | S | 6 | 7.5 | 8.8438 | 0.8 | 88.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.67644 | 0.50733 | Increased | 4KW -> 7.5KW | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 04 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-72-0001-A | Heating Medium Dump Cooler (Bay 1 Fan 1) | N | M-B1 | 0.69 |  | I | 24 | 30 | 33.4197 | 0.8 | 91.6 | 0.82 | 30 | 0 | 0 | 7.8603 | 5.4865 | 0 | 0 | No Change |  | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 04 | 70-IK-61-0003 | B | 70-IK-61-0003B | 70-EA-72-0001-B | Heating Medium Dump Cooler (Bay 1 Fan 2) | N | M-B1 | 0.69 |  | S | 24 | 30 | 33.4197 | 0.8 | 91.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 2.6201 | 1.8288 | No Change |  | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D3 | MS | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-EA-72-0001-C | Heating Medium Dump Cooler (Bay 1 Fan 3) | N | M-B1 | 0.69 |  | I | 24 | 30 | 33.4197 | 0.8 | 91.6 | 0.82 | 30 | 0 | 0 | 7.8603 | 5.4865 | 0 | 0 | No Change |  | Delta-400V, Star-690V |  | 20250105 IOM-ME(MS)-0005 Tag/Description 수정, Voltage 수정 (400V->690V) Tag 수정 (by EL) 20260129 IOM-ME(MS)-0011 Rating 20260203 (△-Y) 20260225 IOM-ME(MS)-0026 DOL 으로 수정, Rating 수정
D4 | MS | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A1 | MEG Regeneration Package - Overhead Condenser (Air cooler) | N | VSD-G2 | 0.69 | VVVF | C | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 100 | 10.5263 | 6.5236 | 0 | 0 | 0 | 0 | Decreased | 50KW -> 10KW |  |  | 20250105 IOM-ME(MS)-0005 Added Tag 수정 (by EL) 20260225 IOM-ME(MS)-0026 VSD (임의 반영) 20260317 IOM-ME(MS)-0032 description 수정
D4 | MS | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A2 | MEG Regeneration Package - Overhead Condenser (Air cooler) | N | VSD-G2 | 0.69 | VVVF | C | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 100 | 10.5263 | 6.5236 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MS)-0032 Added
D4 | MS | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A3 | MEG Regeneration Package - Overhead Condenser (Air cooler) | N | VSD-G2 | 0.69 | VVVF | S | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.0526 | 0.65236 | Added |  |  |  | 20260317 IOM-ME(MS)-0032 Added
D3 | MS | 04 | 70-IK-61-0003 | A | 70-IK-61-0003A | 70-UZ-43-0002-A - SP | MEG Regeneration Package - Overhead Condenser (Air cooler) - Spare | N | VSD-G2 | 0.69 | VVVF | S | 10 | 10 | 10.3621 | 1 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.0526 | 0.65236 | Added |  |  |  | 20260225 IOM-ME(MS)-0026 추가 (임의 반영) 20260225 IOM-ME(MS)-0026 VSD (임의 반영)
D3 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 Main Lube Oil Pump Motor | Export Compressor _ Main LO Pump Motor | N | M-A1 | 0.4 |  | C | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 100 | 28.4211 | 17.6138 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 S/b Lube Oil Pump Motor | Export Compressor _ Standby LO Pump Motor | N | M-A1 | 0.4 |  | S | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.8421 | 1.7614 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 LO reservoir Heater | LO Heater for Export Compressor | N | H2 | 0.4 |  | I | 38.7 | 43 | 76.8609 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 12.2211 | 7.5739 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 용량 수정
D4 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 LO Cooler Fan Motor 1 | Export Compressor _ LO cooler Fan Motor 1 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260105 IOM-ME(MR)-0007 Rating 수정 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 LO Cooler Fan Motor 2 | Export Compressor _ LO cooler Fan Motor 2 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260105 IOM-ME(MR)-0007 Rating, Duty 수정 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 LO Cooler Fan Motor 3 | Export Compressor _ LO cooler Fan Motor 3 | N | M-A1 | 0.4 |  | S | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.94737 | 0.58713 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
B | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1003 Oil Mist Eliminator Fan Motor | Export Compressor _ Oil Mist Eliminator Fan Motor | N | M-A1 | 0.4 |  | C | 0.9 | 1 | 1.7875 | 0.9 | 95 | 0.85 | 100 | 0.94737 | 0.58713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 E-House (incl. VFD Panel) | Export Compressor _ VFD (E-house Low Voltage Power Disctribution for HVAC, water circulation unit, F&G) | N | F | 0.4 |  | C | 72 | 80 | 142.997 | 0.9 | 95 | 0.85 | 100 | 75.7895 | 46.9701 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 수정
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1003 VFD _ Chiller | Export Compressor _ VFD (Cooling Systems - Chiller Package) | N | M-B1 | 0.4 |  | C | 90 | 100 | 178.7462 | 0.9 | 95 | 0.85 | 100 | 94.7368 | 58.7126 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MR)-0016 추가
D3 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 Main Lube Oil Pump Motor | Export Compressor _ Main LO Pump Motor | N | M-A1 | 0.4 |  | C | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 100 | 28.4211 | 17.6138 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 S/b Lube Oil Pump Motor | Export Compressor _ Standby LO Pump Motor | N | M-A1 | 0.4 |  | S | 27 | 30 | 53.6239 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.8421 | 1.7614 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 용량 수정
D3 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 LO reservoir Heater | LO Heater for Export Compressor | N | H2 | 0.4 |  | I | 38.7 | 43 | 76.8609 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 12.2211 | 7.5739 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 용량 수정
D4 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 LO Cooler Fan Motor 1 | Export Compressor _ LO cooler Fan Motor 1 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260105 IOM-ME(MR)-0007 Rating 수정 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 LO Cooler Fan Motor 2 | Export Compressor _ LO cooler Fan Motor 2 | N | M-A1 | 0.4 |  | C | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 100 | 9.4737 | 5.8713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260105 IOM-ME(MR)-0007 Rating, Duty 수정 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
D4 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 LO Cooler Fan Motor 3 | Export Compressor _ LO cooler Fan Motor 3 | N | M-A1 | 0.4 |  | S | 9 | 10 | 17.8746 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.94737 | 0.58713 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260317 IOM-ME(MR)-0007 Rating 수정 (5 -> 10)
B | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-2003 Oil Mist Eliminator Fan Motor | Export Compressor _ Oil Mist Eliminator Fan Motor | N | M-A1 | 0.4 |  | C | 0.9 | 1 | 1.7875 | 0.9 | 95 | 0.85 | 100 | 0.94737 | 0.58713 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 E-House (incl. VFD Panel) | Export Compressor _ VFD (E-house Low Voltage Power Disctribution for HVAC, water circulation unit, F&G) | N | F | 0.4 |  | C | 72 | 80 | 142.997 | 0.9 | 95 | 0.85 | 100 | 75.7895 | 46.9701 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 수정
D4 | MR | 03 (E-House) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-2003 VFD _ Chiller | Export Compressor _ VFD (Cooling Systems - Chiller Package) | N | M-B1 | 0.4 |  | C | 90 | 100 | 178.7462 | 0.9 | 95 | 0.85 | 100 | 94.7368 | 58.7126 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MR)-0016 추가
A | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Aux Lube Oil Pump Motor | Aux LO Pump for Flash Gas Compressor | N | M-A1 | 0.4 |  | I | 4.95 | 5.5 | 9.831 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.5632 | 0.96876 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
A | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Main CW Pump Motor | Main CW Pump Motor for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 100 | 7.1053 | 4.4034 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
A | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Aux CW Pump Motor | Aux CW Pump Motor for Flash Gas Compressor | N | M-A1 | 0.4 |  | S | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.71053 | 0.44034 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
A | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-LO Heater | LO Heater for Flash Gas Compressor | N | H2 | 0.4 |  | I | 2.7 | 3 | 5.3624 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 0.85263 | 0.52841 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
D3 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Coolant Heater | Coolant Heater for Flash Gas Compressor | N | H2 | 0.4 |  | I | 13.5 | 15 | 26.8119 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 4.2632 | 2.6421 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 용량 수정
A | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-Electric Barring Device Motor | Electric Barring Device Motor for Flash Gas Compressor | N | M-A1 | 0.4 |  | I | 1.35 | 1.5 | 2.6812 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 0.42632 | 0.26421 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
A | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-LO Cooler Fan Motor 1 | LO Cooler Fan Motor 1 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 100 | 7.1053 | 4.4034 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
D3 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-LO Cooler Fan Motor 2 | LO Cooler Fan Motor 2 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 100 | 7.1053 | 4.4034 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 description, duty 수정
D3 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-LO Cooler Fan Motor 3 | LO Cooler Fan Motor 3 for Flash Gas Compressor | N | M-A1 | 0.4 |  | S | 6.75 | 7.5 | 13.406 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.71053 | 0.44034 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 1 | CW Console Cooler Fan Motor 1 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 9.9 | 11 | 19.6621 | 0.9 | 95 | 0.85 | 100 | 10.4211 | 6.4584 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
D3 | MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 2 | CW Console Cooler Fan Motor 2 for Flash Gas Compressor | N | M-A1 | 0.4 |  | C | 9.9 | 11 | 19.6621 | 0.9 | 95 | 0.85 | 100 | 10.4211 | 6.4584 | 0 | 0 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260225 IOM-ME(MR)-0014 duty 수정
D3 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-CW Console Cooler Fan Motor 3 | CW Console Cooler Fan Motor 3 for Flash Gas Compressor | N | M-A1 | 0.4 |  | S | 9.9 | 11 | 19.6621 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 1.0421 | 0.64584 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-KA-31-1001/1002-Cylinder Lubricator Heater | Cylinder Lubricator Heater for Flash Gas Compressor | N | H2 | 0.4 |  | I | 0.9 | 1 | 1.7875 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 0.28421 | 0.17614 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0001A Hydraulic Motor | Diesel Firewater Pump A Hydraulic Motor | N | M-A1 | 0.4 |  | S | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.47368 | 0.29356 | Decreased | 15KW -> 5KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정
D3 | MR | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0001A Panel | Diesel Firewater Pump A Enclosure Ventilation Fan Motor | N | M-A1 | 0.4 |  | S | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.47368 | 0.29356 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001B Hydraulic Motor | Diesel Firewater Pump B Hydraulic Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Decreased | 15KW -> 5KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정
D3 | MR | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001B Panel | Diesel Firewater Pump B Enclosure Ventilation Fan Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
A | MR | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001C Hydraulic Motor | Diesel Firewater Pump C Hydraulic Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Decreased | 15KW -> 5KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정
D3 | MR | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0001C Panel | Diesel Firewater Pump C Enclosure Ventilation Fan Motor | N | M-A1 | 0.4 |  | I | 4.5 | 5 | 8.9373 | 0.9 | 95 | 0.85 | 30 | 0 | 0 | 1.4211 | 0.88069 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
| EL | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-HF-01-0002 | Fire water pump control panel | N | F | 0.4 |  | C | 3.8 | 5 | 8.9373 | 0.76 | 95 | 0.85 | 100 | 4 | 2.479 | 0 | 0 | 0 | 0 | No Change |  |  |  | FEED
D3 | MR | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-01-0003A(Main Motor Power) | Firewater Jockey Pump A Motor | N | M-B1 | 0.4 |  | C | 65 | 75 | 136.2103 | 0.86667 | 93.5 | 0.85 | 100 | 69.5187 | 43.0838 | 0 | 0 | 0 | 0 | Increased | 55KW -> 75KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating 수정 20260225 IOM-ME(MR)-0014 Description / Load Type 수정
D3 | MR | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-01-0003B(Main Motor Power) | Firewater Jockey Pump B Motor | N | M-B1 | 0.4 |  | S | 65 | 75 | 136.2103 | 0.86667 | 93.5 | 0.85 | 10 | 0 | 0 | 0 | 0 | 6.9519 | 4.3084 | Increased | 55KW -> 75KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating 수정 20260225 IOM-ME(MR)-0014 Description / Load Type 수정
B | MR | 01 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0001A Motor | Motor for Closed Drains Drum Booster Pump | N | M-A1 | 0.4 |  | I | 1.5 | 3.7 | 7.1412 | 0.40541 | 91.2 | 0.82 | 30 | 0 | 0 | 0.49342 | 0.34441 | 0 | 0 | Decreased | 4KW -> 3.7KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating 수정
B | MR | 01 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0001A Seal Motor | Motor for Closed Drains Drum Booster Pump- Seal Circulation Pump | N | M-A1 | 0.4 |  | I | 0.4 | 0.55 | 1.0615 | 0.72727 | 91.2 | 0.82 | 30 | 0 | 0 | 0.13158 | 0.091843 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 01 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0001B Motor | Motor for Closed Drains Drum Booster Pump | N | M-A1 | 0.4 |  | S | 1.5 | 3.7 | 7.1412 | 0.40541 | 91.2 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.16447 | 0.1148 | Decreased | 4KW -> 3.7KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating 수정
B | MR | 01 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0001B Seal Motor | Motor for Closed Drains Drum Booster Pump- Seal Circulation Pump | N | M-A1 | 0.4 |  | I | 0.4 | 0.55 | 1.0615 | 0.72727 | 91.2 | 0.82 | 30 | 0 | 0 | 0.13158 | 0.091843 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B2 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0004A Motor | Motor for Off spec Water Recycle Pump | N | M-A1 | 0.4 |  | I | 6.02 | 7.5 | 15.2555 | 0.80267 | 88.7 | 0.8 | 30 | 0 | 0 | 2.0361 | 1.5271 | 0 | 0 | Increased | 5.5KW -> 7.5KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating, WBS 수정 20260108 IOM-ECI(EL)-0007 CPR 답변 반영
B | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0004B Motor | Motor for Off spec Water Recycle Pump | N | M-A1 | 0.4 |  | S | 6.02 | 7.5 | 15.2555 | 0.80267 | 88.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.67869 | 0.50902 | Increased | 5.5KW -> 7.5KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20260105 IOM-ME(MR)-0007 Rating, WBS 수정
B | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PS-28-0005A Motor | Motor for Open Drains Treatment Pump | N | M-A1 | 0.4 |  | I | 11.4 | 15 | 30.511 | 0.76 | 88.7 | 0.8 | 30 | 0 | 0 | 3.8557 | 2.8918 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PS-28-0005B Motor | Motor for Open Drains Treatment Pump | N | M-A1 | 0.4 |  | S | 11.4 | 15 | 30.511 | 0.76 | 88.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 1.2852 | 0.96392 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
D4 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven Main LO Pump | N | M-A1 | 0.4 |  | C | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 100 | 5.5 | 3.4086 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven Aux. LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 Rating 수정
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven LO Air Cooler Fan A | N | M-A1 | 0.4 |  | C | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 100 | 3 | 1.8592 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven LO Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | Motor Driven Lubricator | N | M-A1 | 0.4 |  | C | 1.9 | 2 | 3.5749 | 0.95 | 95 | 0.85 | 100 | 2 | 1.2395 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001A | LO Heater | N | M-A1 | 0.4 |  | I | 3 | 3 | 5.3624 | 1 | 95 | 0.85 | 30 | 0 | 0 | 0.94737 | 0.58713 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D4 | MR | 02 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven Main LO Pump | N | M-A1 | 0.4 |  | I | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 1.65 | 1.0226 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 02 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven Aux. LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 Rating 수정
D3 | MR | 02 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven LO Air Cooler Fan A | N | M-A1 | 0.4 |  | I | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 0.9 | 0.55777 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven LO Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | Motor Driven Lubricator | N | M-A1 | 0.4 |  | I | 1.9 | 2 | 3.5749 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 0.6 | 0.37185 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-43-0001B | LO Heater | N | M-A1 | 0.4 |  | I | 3 | 3 | 5.3624 | 1 | 95 | 0.85 | 30 | 0 | 0 | 0.94737 | 0.58713 | 0 | 0 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D4 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven Main LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 Rating 수정
D4 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven Aux. LO Pump | N | M-A1 | 0.4 |  | S | 5.225 | 5.5 | 9.831 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.55 | 0.34086 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가 20260317 IOM-ME(MR)-0016 Rating 수정
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven LO Air Cooler Fan A | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven LO Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 2.85 | 3 | 5.3624 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.3 | 0.18592 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | Motor Driven Lubricator | N | M-A1 | 0.4 |  | S | 1.9 | 2 | 3.5749 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.2 | 0.12395 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-43-0001C | LO Heater | N | M-A1 | 0.4 |  | S | 3 | 3 | 5.3624 | 1 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.31579 | 0.19571 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
| MR | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-31-1003 | 1st Stage FGC Suction Scrubber Pump Motor - Train 1 | N | M-A1 | 0.4 |  | I | 0.032 | 0.75 | 1.6624 | 0.042667 | 81.4 | 0.8 | 30 | 0 | 0 | 0.011794 | 0.0088452 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-43-0001A | Rich MEG Pump | N | M-A1 | 0.4 |  | C | 8.75 | 11 | 21.5616 | 0.79545 | 89.8 | 0.82 | 100 | 9.7439 | 6.8013 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0001B | Rich MEG Pump | N | M-A1 | 0.4 |  | S | 8.75 | 11 | 21.5616 | 0.79545 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.97439 | 0.68013 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
B3 | MS | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-C | MEG Regeneration Package - Lean MEG Pump A | N | M-A1 | 0.4 |  | C | 5.5 | 5.5 | 11.3149 | 1 | 87.7 | 0.8 | 100 | 6.2714 | 4.7035 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 Description 수정 Tag 수정 (by EL)
B3 | MS | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-D | MEG Regeneration Package - Lean MEG Pump B | N | M-A1 | 0.4 |  | S | 5.5 | 5.5 | 11.3149 | 1 | 87.7 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.62714 | 0.47035 | No Change |  |  |  | 20260105 IOM-ME(MR)-0007 Description 수정 Tag 수정 (by EL)
D3 | MS | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-E | MEG Regeneration Package - Reflux Pump A | N | M-A1 | 0.4 |  | C | 30 | 30 | 58.2852 | 1 | 90.6 | 0.82 | 100 | 33.1126 | 23.1127 | 0 | 0 | 0 | 0 | Increased | 15KW -> 30KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정 Tag 수정 (by EL) 20260225 IOM-ME(MS)-0026 Rating 수정
D3 | MS | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-F | MEG Regeneration Package - Reflux Pump B | N | M-A1 | 0.4 |  | S | 30 | 30 | 58.2852 | 1 | 90.6 | 0.82 | 10 | 0 | 0 | 0 | 0 | 3.3113 | 2.3113 | Increased | 15KW -> 30KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정 Tag 수정 (by EL) 20260225 IOM-ME(MS)-0026 Rating 수정
D3 | MS | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-43-0002-G | MEG Regeneration Package - Hydrocarbon Recovery Pump A | N | M-A1 | 0.4 |  | I | 7.55 | 7.55 | 15.7296 | 1 | 86.6 | 0.8 | 30 | 0 | 0 | 2.6155 | 1.9616 | 0 | 0 | Increased | 4KW -> 7.55KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정 Tag 수정 (by EL) 20260225 IOM-ME(MS)-0026 Rating 수정
D3 | MS | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-43-0002-H | MEG Regeneration Package - Hydrocarbon Recovery Pump B | N | M-A1 | 0.4 |  | S | 7.55 | 7.55 | 15.7296 | 1 | 86.6 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.87182 | 0.65387 | Increased | 4KW -> 7.55KW |  |  | 20260105 IOM-ME(MR)-0007 Description 수정 Tag 수정 (by EL) 20260225 IOM-ME(MS)-0026 Rating 수정
| MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-43-0003A | Lean MEG Transfer Pump | N | M-A1 | 0.4 |  | C | 2.5 | 7.5 | 15.8265 | 0.33333 | 85.5 | 0.8 | 100 | 2.924 | 2.193 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0003B | Lean MEG Transfer Pump | N | M-A1 | 0.4 |  | S | 2.5 | 7.5 | 15.8265 | 0.33333 | 85.5 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.2924 | 0.2193 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-43-0004 | MEG Offloading Pump | N | M-A1 | 0.4 |  | I | 3.63 | 7.5 | 15.8265 | 0.484 | 85.5 | 0.8 | 30 | 0 | 0 | 1.2737 | 0.95526 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
C3 | EL | 07 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0054 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Gate house - Indoor (70-IG-62-0054) | N | L | 0.4 |  | C | 2.1 | 5 | 8.9373 | 0.42 | 95 | 0.85 | 100 | 2.2105 | 1.37 | 0 | 0 | 0 | 0 |  |  |  | MAIN GATE HOUSE | 20251216 FEED EQ LIST Added
C3 | EL | 07 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0055 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Access control building Security HUT 02 - Indoor (70-IG-62-0055) | N | L | 0.4 |  | C | 2.1 | 5 | 8.9373 | 0.42 | 95 | 0.85 | 100 | 2.2105 | 1.37 | 0 | 0 | 0 | 0 |  |  |  | SECURITY HUT 02 | FEED
C3 | EL | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0056A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building - Indoor A (70-IG-62-0056A) | N | L | 0.4 |  | C | 26.5 | 30 | 53.6239 | 0.88333 | 95 | 0.85 | 100 | 27.8947 | 17.2876 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0056B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building - Indoor B (70-IG-62-0056B) | N | L | 0.4 |  | C | 29 | 30 | 53.6239 | 0.96667 | 95 | 0.85 | 100 | 30.5263 | 18.9185 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 06 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0059A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Workshop & Warehouse - Indoor A (70-IG-62-0059A) | N | L | 0.4 |  | C | 24.5 | 30 | 53.6239 | 0.81667 | 95 | 0.85 | 100 | 25.7895 | 15.9829 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 06 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0059B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Workshop & Warehouse - Indoor B (70-IG-62-0059B) | N | L | 0.4 |  | C | 26 | 30 | 53.6239 | 0.86667 | 95 | 0.85 | 100 | 27.3684 | 16.9614 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 06 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0060 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Adminstration Building - Indoor (70-IG-62-0060) | N | L | 0.4 |  | C | 24 | 30 | 53.6239 | 0.8 | 95 | 0.85 | 100 | 25.2632 | 15.6567 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 06 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0061 | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Control Building (Laboratory room) - Indoor (70-IG-62-0061) | N | L | 0.4 |  | C | 40 | 50 | 89.3731 | 0.8 | 95 | 0.85 | 100 | 42.1053 | 26.0945 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0062A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Substation - Indoor A (70-IG-62-0062A) | N | L | 0.4 |  | C | 23 | 30 | 53.6239 | 0.76667 | 95 | 0.85 | 100 | 24.2105 | 15.0043 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0062B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - Main Substation - Indoor B (70-IG-62-0062B) | N | L | 0.4 |  | C | 24 | 30 | 53.6239 | 0.8 | 95 | 0.85 | 100 | 25.2632 | 15.6567 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-62-0064A | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - ITR East-Utilities - Indoor A (70-IG-62-0064A) | N | L | 0.4 |  | C | 28 | 30 | 53.6239 | 0.93333 | 95 | 0.85 | 100 | 29.4737 | 18.2661 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0064B | 0.4/0.42kV Dry type Transformer for 400/230V Normal L & SP DB - ITR East-Utilities - Indoor B (70-IG-62-0064B) | N | L | 0.4 |  | C | 25 | 30 | 53.6239 | 0.83333 | 95 | 0.85 | 100 | 26.3158 | 16.3091 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-IV-66-0002 | 0.4/0.42kV Dry type Transformer for 400V Normal Welding Outlet DB- Outdoor A (70-IG-66-0002) | N | F | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 0 | 0 | 59.7267 | 0 |  |  |  |  | 20260120 Added_Franca
C4 | EL | 07 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-IV-62-0099 | 0.4/0.42kV Dry type Transformer for 400/230V Normal DB for EV Charging (70-IG-62-0099) | N | L | 0.4 | [9 empty] | 0 | 0 | 12.6 | 7.8088 | 0 | 0 |  |  |  |  | 20260209 추가
B3 | MS | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-71-0001-A | Diesel Transfer and Filtration Package Pump Motor A | N | M-A1 | 0.4 |  | I | 2.2 | 2.2 | 4.7085 | 1 | 84.3 | 0.8 | 30 | 0 | 0 | 0.78292 | 0.58719 | 0 | 0 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 Tag 수정 Tag 수정 (by EL)
B3 | MS | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-71-0001-B | Diesel Transfer and Filtration Package Pump Motor B | N | M-A1 | 0.4 |  | S | 2.2 | 2.2 | 4.7085 | 1 | 84.3 | 0.8 | 10 | 0 | 0 | 0 | 0 | 0.26097 | 0.19573 | No Change |  |  |  | 20250105 IOM-ME(MS)-0005 Tag 수정 Tag 수정 (by EL)
| MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-72-0001A | Heating Medium Circulation Pump | N | M-B1 | 0.4 |  | C | 79.2 | 90 | 163.4524 | 0.88 | 93.5 | 0.85 | 100 | 84.7059 | 52.496 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-72-0001B | Heating Medium Circulation Pump | N | M-B1 | 0.4 |  | S | 79.2 | 90 | 163.4524 | 0.88 | 93.5 | 0.85 | 10 | 0 | 0 | 0 | 0 | 8.4706 | 5.2496 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
D4 | MS | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-72-0001A (70-HF-72-0001A) | Fired Heater A FD Fan | N | F | 0.4 |  | C | 30 | 30 | 53.6239 | 1 | 95 | 0.85 | 100 | 31.5789 | 19.5709 | 0 | 0 | 0 | 0 | Increased | 10KW -> 30KW |  |  | 20250105 IOM-ME(MS)-0005 Tag/Description/Rating 수정 20260317 Tag 오류 수정 20260317 IOM-ME(MS)-0032 용량 수정
D4 | MS | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-72-0001B (70-HF-72-0001B) | Fired Heater B FD Fan | N | F | 0.4 |  | C | 30 | 30 | 53.6239 | 1 | 95 | 0.85 | 100 | 31.5789 | 19.5709 | 0 | 0 | 0 | 0 | Increased / Duty | 10KW -> 30KW / S -> C |  |  | 20250105 IOM-ME(MS)-0005 Tag/Description/Rating 수정 20260317 Tag 오류 수정 20260317 IOM-ME(MS)-0032 용량 수정
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Pump A | Motor for Pour Point Depressant Injection Package | N | M-A1 | 0.4 |  | C | 1.43 | 1.5 | 2.6812 | 0.95333 | 95 | 0.85 | 100 | 1.5053 | 0.93288 | 0 | 0 | 0 | 0 | Increased / Duty | 0.75KW -> 1.5KW / I -> C |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Pump B | Motor for Pour Point Depressant Injection Package | N | M-A1 | 0.4 |  | S | 1.43 | 1.5 | 2.6812 | 0.95333 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.15053 | 0.093288 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007_Duty 수정 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Agitator | Motor for Agitator | N | M-A1 | 0.4 |  | C | 3.8 | 4 | 7.1498 | 0.95 | 95 | 0.85 | 100 | 4 | 2.479 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UI-75-0001-Filling Pump | Motor for Filling Pump | N | M-A1 | 0.4 |  | I | 2.09 | 2.2 | 3.9324 | 0.95 | 95 | 0.85 | 30 | 0 | 0 | 0.66 | 0.40903 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Pump A | Motor for Corrosion Inhibitor Injection Package | N | M-A1 | 0.4 |  | C | 0.24 | 0.25 | 0.44687 | 0.96 | 95 | 0.85 | 100 | 0.25263 | 0.15657 | 0 | 0 | 0 | 0 | Decreased | 0.75KW -> 0.25KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Pump B | Motor for Corrosion Inhibitor Injection Package | N | M-A1 | 0.4 |  | S | 0.24 | 0.25 | 0.44687 | 0.96 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 0.025263 | 0.015657 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007_Duty 수정 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Agitator | Motor for Agitator | N | M-A1 | 0.4 |  | C | 0.35 | 0.37 | 0.66136 | 0.94595 | 95 | 0.85 | 100 | 0.36842 | 0.22833 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UI-75-0002-Filling Pump | Motor for Filling Pump | N | M-A1 | 0.4 |  | I | 0.71 | 0.75 | 1.3406 | 0.94667 | 95 | 0.85 | 30 | 0 | 0 | 0.22421 | 0.13895 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-75-0001-Pump A | Motor for MEG Injection Package | N | M-A1 | 0.4 |  | C | 20.9 | 22 | 39.3242 | 0.95 | 95 | 0.85 | 100 | 22 | 13.6344 | 0 | 0 | 0 | 0 | Increased | 5KW -> 22KW |  |  | 20251202 IOM-ME(MR)-0003 수정 20251216 Load Type 수정 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-75-0001-Pump B | Motor for MEG Injection Package | N | M-A1 | 0.4 |  | S | 20.9 | 22 | 39.3242 | 0.95 | 95 | 0.85 | 10 | 0 | 0 | 0 | 0 | 2.2 | 1.3634 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정 20260109 RE: [AGSA] Load List 확인 요청 건 / IOM-ME(MR)-0007_Duty 수정 20260128 IOM-ME(MR)-0010 Rating 수정
| MR | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-DM-85-0001A | Utility Water Pump A Motor | N | M-A1 | 0.4 |  | S | 5.8 | 11 | 21.5616 | 0.52727 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.64588 | 0.45083 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-DM-85-0001B | Utility Water Pump B Motor | N | M-A1 | 0.4 |  | C | 5.8 | 11 | 21.5616 | 0.52727 | 89.8 | 0.82 | 100 | 6.4588 | 4.5083 | 0 | 0 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 01 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-PA-28-0007A | Closed Drains Pump | N | M-A1 | 0.4 |  | I | 11.3 | 15 | 29.4022 | 0.75333 | 89.8 | 0.82 | 30 | 0 | 0 | 3.7751 | 2.635 | 0 | 0 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
| MR | 01 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-PA-28-0007B | Closed Drains Pump | N | M-A1 | 0.4 |  | S | 11.3 | 15 | 29.4022 | 0.75333 | 89.8 | 0.82 | 30 | 0 | 0 | 0 | 0 | 3.7751 | 2.635 | No Change |  |  |  | 20251202 IOM-ME(MR)-0003 수정
D3 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-Liquid Ring Recirculation Pump | Motor for Liquid Ring Recirculation Pump A | N | M-A1 | 0.4 |  | C | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 100 | 15.0334 | 10.4934 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-Liquid Ring Recirculation Pump | Motor for Liquid Ring Recirculation Pump B | N | M-A1 | 0.4 |  | S | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.5033 | 1.0493 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
D3 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-Liquid Ring Air Cooler | Motor for Liquid Ring Air Cooler Fan A | N | M-A1 | 0.4 |  | C | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 100 | 15.0334 | 10.4934 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가 20260225 IOM-ME(MR)-0014 Description 수정
D3 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-Liquid Ring Air Cooler | Motor for Liquid Ring Air Cooler Fan B | N | M-A1 | 0.4 |  | S | 13.5 | 15 | 29.4022 | 0.9 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.5033 | 1.0493 | Added |  |  |  | 20260225 IOM-ME(MR)-0014 추가
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UZ-36-0003-LO Heater for 70-KG-36-0003A | LO Heater for Liquid Ring Compressor (70-KG-36-0003A) | N | H2 | 0.4 |  | I | 2.7 | 3 | 5.8804 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 0.902 | 0.6296 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UZ-36-0003-LO Heater for 70-KG-36-0003B | LO Heater for Liquid Ring Compressor (70-KG-36-0003B) | N | H2 | 0.4 |  | I | 2.7 | 3 | 5.8804 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 0.902 | 0.6296 | 0 | 0 | Added |  |  |  | 20260128 IOM-ME(MR)-0010 추가
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.1 | Aeration system(Rotor) A for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.1.2 | Aeration system(Rotor) B for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.3 | Aeration system(Rotor) C for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.1.4 | Aeration system(Rotor) D for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260128 IOM-ME(MR)-0010 Rating 수정
C1 | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 2.1.5 | Skimmer for IAF Unit | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260128 IOM-ME(MR)-0010 Rating 수정
D4 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.2.1 | FLOAT OILY SLUDGE PUMP A (included in 70-UU-28-0001) | N | M-A1 | 0.4 |  | C | 1.76 | 2.2 | 4.3123 | 0.8 | 89.8 | 0.82 | 100 | 1.9599 | 1.368 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added 20260317 IOM-ME(MR)-0016 Tag/Description 수정
D4 | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 2.2.2 | FLOAT OILY SLUDGE PUMP A (included in 70-UU-28-0001) | N | M-A1 | 0.4 |  | C | 1.76 | 2.2 | 4.3123 | 0.8 | 89.8 | 0.82 | 100 | 1.9599 | 1.368 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ME(MR)-0016 Added
B | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 3.1 | Dosing Pump_A_Demulsifying Chemical Dosing System | N | M-A1 | 0.4 |  | C | 0.32 | 0.4 | 0.78406 | 0.8 | 89.8 | 0.82 | 100 | 0.35635 | 0.24873 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UU-28-0001_Sub Item 3.2 | Dosing Pump_B_Demulsifying Chemical Dosing System | N | M-A1 | 0.4 |  | S | 0.32 | 0.4 | 0.78406 | 0.8 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 0.035635 | 0.024873 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
B | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UU-28-0001_Sub Item 4 | Agitator_Demulsifying Chemical Dosing System | N | M-A1 | 0.4 |  | C | 0.6 | 0.75 | 1.4701 | 0.8 | 89.8 | 0.82 | 100 | 0.66815 | 0.46637 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
A | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JC-78-0003 | Overhead Crane - Workshop Building (10 Te SWL) | N | F | 0.4 |  | I | 9 | 10 | 19.6015 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 3.0067 | 2.0987 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added 20251216 Load Type 수정
D | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JH-78-0001 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
D | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-JH-78-0002 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
D | MR | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-JH-78-0003 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
D | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-JH-78-0004 | Power Hoists (various capacities) | N | F | 0.4 |  | I | 4.5 | 5 | 9.8007 | 0.9 | 89.8 | 0.82 | 30 | 0 | 0 | 1.5033 | 1.0493 | 0 | 0 | Added |  |  |  | 20251202 IOM-ME(MR)-0003 Added
B | MR | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | EV-0001 (Temp) | Elevator | Em | F | 0.4 |  | I | 15.2 | 18 | 35.2827 | 0.84444 | 89.8 | 0.82 | 30 | 0 | 0 | 5.078 | 3.5444 | 0 | 0 | Added |  |  |  | 20260105 IOM-ME(MR)-0007 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-CEMS-72-0001A (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (Lighting & etc. for 70-UZ-72-0001A) | N | F | 0.4 |  | C | 1.79 | 1.79 | 3.5087 | 1 | 89.8 | 0.82 | 100 | 1.9933 | 1.3913 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-CEMS-72-0001B (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (Lighting & etc. for 70-UZ-72-0001B) | N | F | 0.4 |  | C | 1.79 | 1.79 | 3.5087 | 1 | 89.8 | 0.82 | 100 | 1.9933 | 1.3913 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-CEMS-72-0001C (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001A) - Primary | N | F | 0.4 |  | C | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 100 | 12.5835 | 8.7834 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-CEMS-72-0001D (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001B) - Primary | N | F | 0.4 |  | C | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 100 | 12.5835 | 8.7834 | 0 | 0 | 0 | 0 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-CEMS-72-0001E (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001A) - Redundant | N | F | 0.4 |  | S | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.2584 | 0.87834 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 04 (72) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-CEMS-72-0001F (HOLD) | CEMS (Continuos Emission Management System) Shelter for Fired Heater (HVAC for 70-UZ-72-0001B) - Redundant | N | F | 0.4 |  | S | 11.3 | 11.3 | 22.1497 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 1.2584 | 0.87834 | Added |  |  | CEMS SHELTER | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-26-0001 | Analyser House for Condensate Export Metering Package (Lighting & etc.) | N | F | 0.4 |  | C | 2.4 | 2.4 | 4.7044 | 1 | 89.8 | 0.82 | 100 | 2.6726 | 1.8655 | 0 | 0 | 0 | 0 | Added |  |  | 26 (아래 Plotplan 상 Location 참조) | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 03 (35) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0002/0003/0004 | Analyser House for SCP Export, DGN Export and Buy-back Gas Metering Package (Lighting & etc.) | N | F | 0.4 |  | C | 2.4 | 2.4 | 4.7044 | 1 | 89.8 | 0.82 | 100 | 2.6726 | 1.8655 | 0 | 0 | 0 | 0 | Added |  |  | 35 (아래 Plotplan 상 Location 참조) | 20260108 IOM-ECI(EL)-0007 Added
D4 | CI | 03 (26) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-26-0001 (HVAC) | Analyser House for Condensate Export Metering Package (HVAC) - Primary | N | F | 0.4 |  | C | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 100 | 22.2717 | 15.5458 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (35) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0002/0003/0004 (HVAC) | Analyser House for SCP Export, DGN Export and Buy-back Gas Metering Package (HVAC) - Primary | N | F | 0.4 |  | C | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 100 | 22.2717 | 15.5458 | 0 | 0 | 0 | 0 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-UN-26-0001 (HVAC) | Analyser House for Condensate Export Metering Package (HVAC) - Redundant | N | F | 0.4 |  | S | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 2.2272 | 1.5546 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (35) | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-UN-35-0002/0003/0004 (HVAC) | Analyser House for SCP Export, DGN Export and Buy-back Gas Metering Package (HVAC) - Redundant | N | F | 0.4 |  | S | 20 | 20 | 39.203 | 1 | 89.8 | 0.82 | 10 | 0 | 0 | 0 | 0 | 2.2272 | 1.5546 | Added |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D | EL | 12 | 70-IK-61-0002 | A | 70-IK-61-0002A | 82-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Production Inlet | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | B | 70-IK-61-0002B | 83-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Gas Export | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | A | 70-IK-61-0002A | 84-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Condensate | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | B | 70-IK-61-0002B | 86-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - MEG | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 12 | 70-IK-61-0002 | A | 70-IK-61-0002A | 87-TRU-87-0001 | Cathodic Protection Transformer/Rectifier for Onshore Pipelines - Domestic Gas Export | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1001 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1002 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1011 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1012 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1013 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1014 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 04 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1003 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 04 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1004 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 04 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 03 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1005 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 03 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 03 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1006 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 03 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 02 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1007 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 02 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 02 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1008 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 02 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 01 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1009 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 01 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 01 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1010 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 01 Pipelines | N | F | 0.4 |  | C | 3 | 3 | 5.0645 | 1 | 95 | 0.9 | 100 | 3.1579 | 1.5294 | 0 | 0 | 0 | 0
D | EL | 05 | 70-IK-61-0002 | B | 70-IK-61-0002B | 70-TRU-87-1015 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
D | EL | 05 | 70-IK-61-0002 | A | 70-IK-61-0002A | 70-TRU-87-1016 | Cathodic Protection Transformer/Rectifier for In Plant Facilities - Unit 05 Tank | N | F | 0.4 |  | C | 2 | 2 | 3.3763 | 1 | 95 | 0.9 | 100 | 2.1053 | 1.0196 | 0 | 0 | 0 | 0
C4 | EL | 07 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 1 | EV Charging - 1 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 07 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 2 | EV Charging - 2 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 07 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 3 | EV Charging - 3 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 07 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 4 | EV Charging - 4 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 07 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 5 | EV Charging - 5 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
C4 | EL | 07 | 70-IG-62-0099 |  | 70-IG-62-0099 | EV Charging - 6 | EV Charging - 6 | N | F | 0.4 |  | I | 6.3 | 7 | 13.2074 | 0.9 | 90 | 0.85 | 30 | 0 | 0 | 2.1 | 1.3015 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1001 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (1 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1002 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (2 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1003 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (3 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1004 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (4 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1005 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (5 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1006 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (6 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1007 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering SBB (7 of 7) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1008 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (8 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1009 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (9 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1010 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (10 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1011 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (11 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1012 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (12 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1013 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (13 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1014 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (14 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1015 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (15 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D4 | CI | 03 (26) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-26-1016 | MOV (Motor Operated Valve) for 70-UN-26-0001 Metering DBB (16 of 16) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  |  | 20260317 IOM-ECI(EL)-0031 Added
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2001 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (1 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2002 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (2 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2003 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (3 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2004 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (4 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2005 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (5 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2006 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (6 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2007 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (7 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2008 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (8 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2009 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (9 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-2010 | MOV (Motor Operated Valve) for 70-UN-35-0002 Metering DBB (10 of 10) | N | F | 0.4 |  | I | 3.24 | 4.3 | 5.7 | 0.75349 | 90 | 0.82 | 30 | 0 | 0 | 1.08 | 0.75384 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3001 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (1 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3002 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (2 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3003 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (3 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3004 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (4 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3005 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (5 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3006 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (6 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3007 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (7 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3008 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (8 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3009 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (9 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-3010 | MOV (Motor Operated Valve) for 70-UN-35-0003 Metering DBB (10 of 10) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4001 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (1 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4002 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (2 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4003 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (3 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 03 (35) | 70-IG-62-0017 |  | 70-IG-62-0017 | 70-MOV-35-4004 | MOV (Motor Operated Valve) for 70-UN-35-0004 Metering DBB (4 of 4) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0001 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0 |  |  |  | AT THE INLET OF 70-VP-10-0001 | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0002 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 2.61 | 2.9 | 4.59 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.87 | 0.60726 | 0 | 0 |  |  |  | AT THE INLET OF 70-VP-10-0001 | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0003 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-VP-10-0001 TO SLUG CATCHERS | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0004 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-VP-10-0001 TO SLUG CATCHERS | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 02 (10) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-10-0005 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 3.87 | 4.3 | 6.81 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 1.29 | 0.90043 | 0 | 0 |  |  |  | FROM SUBSEA PRODUCTION FLOWLINE TO CHOKE VALVES | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 03 (25) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-25-0021 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-UN-26-0001 TO 70-VP-25-0001 | 20260108 IOM-ECI(EL)-0007 Added
D2 | CI | 03 (25) | 70-IG-62-0018 |  | 70-IG-62-0018 | 70-MOV-25-0022 | MOV (Motor Operated Valve) | N | F | 0.4 |  | I | 1.53 | 1.7 | 2.69 | 0.9 | 90 | 0.82 | 30 | 0 | 0 | 0.51 | 0.35598 | 0 | 0 |  |  |  | FROM 70-UN-26-0001 TO SD2 AT SANGACHAL TERMINAL | 20260108 IOM-ECI(EL)-0007 Added
C | EL | 01 | 70-IG-66-0001 |  | 70-IG-66-0001 | 01-WO-0001 | Welding Socket Outlet X 2EA (01-WO-01 & 01-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
D | EL | 01 | 70-IG-66-0001 |  | 70-IG-66-0001 | 01-WO-0002 | Welding Socket Outlet X 2EA (01-WO-03 & 01-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  | Flare stack area에 2ea 반영 |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 02 | 70-IG-66-0001 |  | 70-IG-66-0001 | 02-WO-0001 | Welding Socket Outlet X 2EA (02-WO-01 & 02-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 02 | 70-IG-66-0001 |  | 70-IG-66-0001 | 02-WO-0002 | Welding Socket Outlet X 2EA (02-WO-03 & 02-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 03 | 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0001 | Welding Socket Outlet X 2EA (03-WO-01 & 03-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 03 | 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0002 | Welding Socket Outlet X 2EA (03-WO-03 & 03-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 03 | 70-IG-66-0001 |  | 70-IG-66-0001 | 03-WO-0003 | Welding Socket Outlet X 2EA (03-WO-05 & 03-WO-06) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 04 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0001 | Welding Socket Outlet X 2EA (04-WO-01 & 04-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 04 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0002 | Welding Socket Outlet X 2EA (04-WO-03 & 04-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 04 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0003 | Welding Socket Outlet X 2EA (04-WO-05 & 04-WO-06) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 04 | 70-IG-66-0001 |  | 70-IG-66-0001 | 04-WO-0004 | Welding Socket Outlet X 2EA (04-WO-07 & 04-WO-08) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 05 | 70-IG-66-0002 |  | 70-IG-66-0002 | 05-WO-0001 | Welding Socket Outlet X 2EA (05-WO-01 & 05-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 05 | 70-IG-66-0002 |  | 70-IG-66-0002 | 05-WO-0002 | Welding Socket Outlet X 2EA (05-WO-03 & 05-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 06 | 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0001 | Welding Socket Outlet X 2EA (06-WO-01 & 06-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 06 | 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0002 | Welding Socket Outlet X 2EA (06-WO-03 & 06-WO-04) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
D | EL | 06 | 70-IG-66-0002 |  | 70-IG-66-0002 | 06-WO-0003 | Welding Socket Outlet X 1EA (06-WO-05) | N | F | 0.4 |  | S | 43.6464 | 43.6464 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 4.5944 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
D | EL | 07 | 70-IG-66-0002 |  | 70-IG-66-0002 | 07-WO-0001 | Welding Socket Outlet X 2EA (07-WO-01 & 07-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  | Parking area (Plant entrance area) 1ea |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C | EL | 08 | 70-IG-66-0002 |  | 70-IG-66-0002 | 08-WO-0001 | Welding Socket Outlet X 2EA (08-WO-01 & 08-WO-02) | N | F | 0.4 |  | S | 87.2928 | 87.2928 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 9.1887 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정
C3 | EL | 03 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0065A | 400/230V Normal L & SP DB - ITR West-Process - Indoor A | N | L | 0.4 |  | C | 21 | 30 | 53.6239 | 0.7 | 95 | 0.85 | 100 | 22.1053 | 13.6996 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 03 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0065B | 400/230V Normal L & SP DB - ITR West-Process - Indoor B | N | L | 0.4 |  | C | 26 | 30 | 53.6239 | 0.86667 | 95 | 0.85 | 100 | 27.3684 | 16.9614 | 0 | 0 | 0 | 0 |  |  |  |  | FEED
C3 | EL | 03 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-62-0066 | 400/230V Normal L & SP DB - Process - Outdoor | N | L | 0.4 |  | C | 32 | 40 | 71.4985 | 0.8 | 95 | 0.85 | 100 | 33.6842 | 20.8756 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 FEED EQ LIST Added
C3 | EL | 03 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-65-0084 | 400/230V Heat Tracing - Booster and Flash Gas Compressor area - Outdoor | N | PDB | 0.4 |  | C | 40 | 85 | 129.1441 | 0.47059 | 95 | 1 | 100 | 42.1053 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 Load Type 수정
C3 | EL | 02 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-65-0085 | 400/230V Heat Tracing - Slug Catcher Vapour recovery area - Outdoor | N | PDB | 0.4 |  | C | 40 | 85 | 129.1441 | 0.47059 | 95 | 1 | 100 | 42.1053 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 Load Type 수정
C3 | EL | 05 | 70-IG-62-0093 |  | 70-IG-62-0093 | 70-IG-66-0001 | 400V Normal Welding Outlet DB- Outdoor B | N | F | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 0 | 0 | 59.7267 | 0 |  |  |  |  | 20260120 Added_Franca
C5 | EL | 03 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0012 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor A | Em | L | 0.4 |  | C | 14.3 | 15 | 25.4713 | 0.95333 | 100 | 0.85 | 100 | 14.3 | 8.8623 | 0 | 0 | 0 | 0 |  |  |  | ITR WEST | FEED
C5 | EL | 03 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0053 | 400/230V Emergency L & SP DB - ITR West-Process - Indoor B | Em | L | 0.4 |  | C | 23.7 | 32 | 54.3388 | 0.74062 | 100 | 0.85 | 100 | 23.7 | 14.6879 | 0 | 0 | 0 | 0 |  |  |  | ITR WEST | FEED
C3 | EL | 03 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0019 | 400/230V Emergency L & SP DB - Process - Outdoor | Em | L | 0.4 |  | C | 32 | 40 | 67.9236 | 0.8 | 100 | 0.85 | 100 | 32 | 19.8318 | 0 | 0 | 0 | 0 |  |  |  |  | 20251216 FEED EQ LIST Added
C3 | EL | 03 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0081 | 400/230V Emergency Heat Tracing DB - Booster and Flash Gas Compressor area - Outdoor | Em | PDB | 0.4 |  | C | 60 | 85 | 122.6869 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FEED 20251216 Load Type 수정
C3 | EL | 02 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0082 | 400/230V Emergency Heat Tracing DB - Slug Catcher Vapour recovery area - Outdoor | Em | PDB | 0.4 |  | C | 60 | 85 | 122.6869 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FEED 20251216 Load Type 수정
C3 | EL | 04 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-65-0083 | 400/230V Emergency Heat Tracing DB - Chemical & Utilities area - Outdoor | Em | PDB | 0.4 |  | C | 60 | 85 | 122.6869 | 0.70588 | 100 | 1 | 100 | 60 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | FEED 20251216 Load Type 수정
C4 | EL | 03 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0017 | MOV DB - CPF - Outdoor - Booster compressor | Em | PDB | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 29.7 | 20.7307 | 0 | 0 |  |  | CI Inform Rating 반영 |  | FEED 20251216 Load Type 수정
C4 | EL | 02 | 70-IG-62-0094 |  | 70-IG-62-0094 | 70-IG-62-0018 | MOV DB - CPF - Outdoor - Slug Catcher | Em | PDB | 0.4 |  | C | [6 empty] | 100 | 0 | 0 | 5.07 | 3.5389 | 0 | 0 |  |  | CI Inform Rating 반영 |  | FEED 20251216 Load Type 수정
D5 | EL | 09 | 81-IG-62-0001 |  | Beach Valve | 09-WO-0001 | Welding Socket Outlet X 1EA (09-WO-01) | N | F | 0.4 |  | S | 43.6464 | 43.6464 | 63 | 1 | 95 | 1 | 10 | 0 | 0 | 0 | 0 | 4.5944 | 0 |  |  |  |  | 20251216 강동현 책임님 메일 Added 20260120 Dry TR 추가, 용량 수정 | DELETE

## BV Load List (hidden)
Tag No. | Description | Voltage | Breaker Rating | Location | Switchgear Tag
81-1K-61-0001 | 400V Emergency Switchgear | 400V | 3P 160A MCCB | Beach Valve Station | 81-1K-E1-0001
81-IG-62-0001 | 400/230V Emergency L&SP DB | 400V | 3P 80A MCCB | Node E | 81-1K-E1-0001
81-IK-09-0001A | 400V HVAC MCC Switchgear 1A | 400V | 3P 100A MCCB | Node E | 81-1K-E1-0001
81-IK-09-0001B | 400V HVAC MCC Switchgear 1B | 400V | 3P 100A MCCB | Node E | 81-1K-E1-0001
81-GU-06-0001A | 230V AC UPS for Telecoms | 400V | 3P 40A MCCB | Node E | 81-1K-E1-0001
81-GU-06-0001B | 230V AC UPS for Telecoms | 400V | 3P 40A MCCB | Node E | 81-1K-E1-0001
81-GU-06-0002A | 230V AC UPS for Instrument | 400V | 3P 40A MCCB | Node E | 81-1K-E1-0001
81-GU-06-0002B | 230V AC UPS for Instrument | 400V | 3P 40A MCCB | Node E | 81-1K-E1-0001
SPARE | Spare Feeder | 400V | 3P 100A MCCB | Node E | 81-1K-E1-0001
SPARE | Spare Feeder | 400V | 3P 40A MCCB | Node E | 81-1K-E1-0001
|  |  | 3P 160A MCCB | 1
|  |  | 3P 80A MCCB | 1
|  |  | 3P 100A MCCB | 3
|  |  | 3P 40A MCCB | 5

## EEL
S.No | Revision | Equipment Tag number | Equipment designation | Rated current | Rated Power | UOM | Rated voltage (kV) | Earthing System | GS reference | Equipment Data | Equipment Description | Reference Documents | Location | Overall dimensions (LxWxH)mm Refer to Note 2 | Weight (kq) | Comments
1 | 01 | 70-IV-61-0001A | 11/0.72kV Transformer | _ | 4000 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary: IT (fault limited to 150mA) | GS EP ELE 141 | 4000 kVA, 11/0.72 kV, Dyn11, ONAN, DETC +/- 5% (Steps of +/- 2.5), Z=7% | Enclosure :Hermetically Sealed Connection : (Primary (Cable) / Secondary (Busduct) OLTC : Not applicable CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Oil-immersed power transformer AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List | Main Substation | 2700 X 2700 X 3050 | Note - 4
2 | 01 | 70-IV-61-0001B | 11/0.72kV Transformer | _ | 4000 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary: IT (fault limited to 150mA) | GS EP ELE 141 | 4000 kVA, 11/0.72 kV, Dyn11, ONAN, DETC +/- 5% (Steps of +/- 2.5), Z=7% | Enclosure :Hermetically Sealed Connection : (Primary (Cable) / Secondary (Busduct) OLTC : Not applicable CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Oil-immersed power transformer AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List | Main Substation | 2700 X 2700 X 3050 | Note - 4
3 | 01 | 70-IV-61-0001C | 11/0.72kV Transformer Emergency | _ | 2500 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary: IT (fault limited to 150mA) | GS EP ELE 141 | 2500 kVA, 11/0.72 kV, Dyn11, ONAN, DETC +/- 5% (Steps of +/- 2.5), Z=6% | Enclosure :Hermetically Sealed Connection : (Primary (Cable) / Secondary (Busduct) OLTC : Not applicable CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Oil-immersed power transformer AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List | Main Substation | 1950 X 1350 X 2300 | Note - 4
4 | 01 | 70-IV-61-0003A | 11/0.72kV Transformer | _ | 4000 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary: IT (fault limited to 150mA) | GS EP ELE 141 | 4000 kVA, 11/0.72 kV, Dyn11, ONAN, DETC +/- 5% (Steps of +/- 2.5), Z=7% | Enclosure :Hermetically Sealed Connection : (Primary (Cable) / Secondary (Busduct) OLTC : Not applicable CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Oil-immersed power transformer AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List | Main Substation | 2700 X 2700 X 3050 | Note - 4
5 | 01 | 70-IV-61-0003B | 11/0.72kV Transformer | _ | 4000 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary: IT (fault limited to 150mA) | GS EP ELE 141 | 4000 kVA, 11/0.72 kV, Dyn11, ONAN, DETC +/- 5% (Steps of +/- 2.5), Z=7% | Enclosure :Hermetically Sealed Connection : (Primary (Cable) / Secondary (Busduct) OLTC : Not applicable CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Oil-immersed power transformer AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List | Main Substation | 2700 X 2700 X 3050 | Note - 4
6 | 00 | 70-IV-61-0002A | 11/0.42kV Transformer | _ | 2500 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary: IT (fault limited to 150mA) | GS EP ELE 141 | 2500kVA, 11/0.42kV, Dyn11, ONAN, DETC +/- 5% (Steps of +/- 2.5), Z=6% | Enclosure :Hermetically Sealed Connection : (Primary (Cable) / Secondary (Busduct) OLTC : Not applicable CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Oil-immersed power transformer AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List | Main Substation | 1950 X 1350 X 2300 | Note - 4
7 | 00 | 70-IV-61-0002B | 11/0.42kV Transformer | _ | 2500 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary: IT (fault limited to 150mA) | GS EP ELE 141 | 2500kVA, 11/0.42kV, Dyn11, ONAN, DETC +/- 5% (Steps of +/- 2.5), Z=6% | Enclosure :Hermetically Sealed Connection : (Primary (Cable) / Secondary (Busduct) OLTC : Not applicable CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Oil-immersed power transformer AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List | Main Substation | 1950 X 1350 X 2300 | Note - 4
8 | 00 | 70-IRR-61-0001A | Neutral Earthing Resistor for transformer 70-IV-61-0001A | 150 | _ | mA | 0.69 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.69kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Part of Switchgear | Part of Switchgear
9 | 00 | 70-IRR-61-0001B | Neutral Earthing Resistor for transformer 70-IV-61-0001B | 150 | _ | mA | 0.69 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.69kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Part of Switchgear | Part of Switchgear
10 | 00 | 70-IRR-61-0001C | Neutral Earthing Resistor for transformer 70-IV-61-0001C | 150 | _ | mA | 0.69 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.69kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Part of Switchgear | Part of Switchgear
11 | 00 | 70-IRR-61-0003A | Neutral Earthing Resistor for transformer 70-IV-61-0003A | 150 | _ | mA | 0.69 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.69kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Part of Switchgear | Part of Switchgear
12 | 00 | 70-IRR-61-0003B | Neutral Earthing Resistor for transformer 70-IV-61-0003B | 150 | _ | mA | 0.69 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.69kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Part of Switchgear | Part of Switchgear
13 | 00 | 70-IRR-61-0002A | Neutral Earthing Resistor for transformer 70-IV-61-0002A | 150 | _ | mA | 0.4 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.4kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Part of Switchgear | Part of Switchgear
14 | 00 | 70-IRR-61-0002B | Neutral Earthing Resistor for transformer 70-IV-61-0002B | 150 | _ | mA | 0.4 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.4kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Part of Switchgear | Part of Switchgear
15 | 01 | 70-BDU-61-0001A | Busduct for 690V Switchgear - 1 A | 4000 | _ | A | 0.69 | _ | GS EP ELE 135 | 0.72kV, 4000A, 80kA for 1 sec. | _ | GS EP ELE 001 - Electrical Design Criteria AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Note - 8 | Note - 4
16 | 01 | 70-BDU-61-0001B | Busduct for 690V Switchgear - 1 B | 4000 | _ | A | 0.69 | _ | GS EP ELE 135 | 0.72kV, 4000A, 80kA for 1 sec. | _ | GS EP ELE 001 - Electrical Design Criteria AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Note - 8 | Note - 4
17 | 01 | 70-BDU-61-0001C | Busduct for 690V Switchgear - 1 C | 2500 | _ | A | 0.69 | _ | GS EP ELE 135 | 0.72kV, 2500A, 80kA for 1 sec. | _ | GS EP ELE 001 - Electrical Design Criteria AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Note - 8 | Note - 4
18 | 01 | 70-BDU-61-0003A | Busduct for 690V Switchgear - 2 A | 4000 | _ | A | 0.69 | _ | GS EP ELE 135 | 0.72kV, 4000A, 80kA for 1 sec. | _ | GS EP ELE 001 - Electrical Design Criteria AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Note - 8 | Note - 4
19 | 01 | 70-BDU-61-0003B | Busduct for 690V Switchgear - 2 B | 4000 | _ | A | 0.69 | _ | GS EP ELE 135 | 0.72kV, 4000A, 80kA for 1 sec. | _ | GS EP ELE 001 - Electrical Design Criteria AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Note - 8 | Note - 4
20 | 01 | 70-BDU-61-0002A | Busduct for 400V Switchgear A | 4000 | _ | A | 0.4 | _ | GS EP ELE 135 | 0.42kV, 4000A, 80kA for 1 sec. | _ | GS EP ELE 001 - Electrical Design Criteria AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Note - 8 | Note - 4
21 | 01 | 70-BDU-61-0002B | Busduct for 400V Switchgear B | 4000 | _ | A | 0.4 | _ | GS EP ELE 135 | 0.42kV, 4000A, 80kA for 1 sec. | _ | GS EP ELE 001 - Electrical Design Criteria AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | Note - 8 | Note - 4
22 | 01 | 70-IJ-61-0001 | 11kV Switchgear | 4000 | _ | A | 11 | Resistance Earthed - 20-50A (Refer Note - 10) | GS EP ELE 131 | 11kV, 4000A, 50Hz, 40kA for 1 sec. | Insulation type : Air IAC type : AFLR Withdrawable - LSC2B-PM Equipped with Electrical and Mechanical Interlocks and Surge arrestors. Communication Protocol: Modbus + IEC 61850 Protection Relays : Digital.As per P&M diagrams Circuit details: Incomer - 3 nos Bus - tie - 2 Nos Outgoing feeders - Refer - Electrical Load List | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 131 - High Voltage Switchgear and controlgear assemblies according to IOGP S-620 AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout AZ-AB1-70-SK02-162007 - Typical Protection Diagrams | Main Substation | 25300 x 1455 x 2696 | Note - 4
23 | 01 | 70-IK-61-0001 | 690V Switchgear - 1 | 4000 | _ | A | 0.69 | IT (High Impedance earthed) Impedance limiting earth fault to 150 mA. Refer to Note - 10 | GS EP ELE 135 | 0.69 kV, 4000A, 50Hz, 80kA for 1 sec. | Insulation type : Air Arcing Class B Withdrawable - LSC2B-PM Equipped with Electrical and Mechanical Interlocks. Communication Protocol: Modbus + IEC 61850 Protection: As per P&M diagrams Circuit details: Incomer - 3 nos Bus - tie - 2 Nos Outgoing feeders - Refer to Doc. No.AZ-AB1-70-SK02-160008 - Electrical Load List | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 135 - Low Voltage Switchgear and controlgear assemblies according to IOGP S-560 AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout AZ-AB1-70-SK02-162007 - Typical Protection Diagrams | Main Substation | 21000 x 1000 x 2200 | Note - 4
24 | 01 | 70-IK-61-0003 | 690V Switchgear - 2 | 4000 | _ | A | 0.69 | IT (High Impedance earthed) Impedance limiting earth fault to 150 mA. Refer to Note - 10 | GS EP ELE 135 | 0.69 kV, 4000A, 50Hz, 80kA for 1 sec. | Insulation type : Air Arcing Class B Withdrawable - LSC2B-PM Equipped with Electrical and Mechanical Interlocks. Communication Protocol: Modbus + IEC 61850 Protection: As per P&M diagrams Circuit details: Incomer - 2 nos Bus - tie - 1 No Outgoing feeders - Refer to Doc. No.AZ-AB1-70-SK02-160008 - Electrical Load List | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 135 - Low Voltage Switchgear and controlgear assemblies according to IOGP S-560 AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout AZ-AB1-70-SK02-162007 - Typical Protection Diagrams | Main Substation | 8600 x 1000 x 2200 | Note - 4
25 | 01 | 70-IK-61-0002 | 400V Switchgear | 4000 | _ | A | 0.4 | IT (High Impedance earthed) Impedance limiting earth fault to 150 mA. Refer to Note - 10 | GS EP ELE 135 | 0.4 kV, 4000A, 50Hz, 80kA for 1 sec. | Insulation type : Air Arcing Class B Withdrawable - LSC2B-PM Equipped with Electrical and Mechanical Interlocks and Surge arrestors. Communication Protocol: Modbus + IEC 61850 Protection: As per P&M diagrams Circuit details: Incomer - 2 nos Bus - tie - 1 No Outgoing feeders - Refer to Doc. No.AZ-AB1-70-SK02-160008 - Electrical Load List | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 135 - Low Voltage Switchgear and controlgear assemblies according to IOGP S-560 AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout AZ-AB1-70-SK02-162007 - Typical Protection Diagrams | Main Substation | 16600 x 1000 x 2500 | Note - 4
26 | 01 | 70-IV-62-0001 | 0.69/0.42kV Emergency L & SP Transformer - Main Gate house -Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Gate House | Part of Lighting Distribution board | Part of Lighting Distribution board
27 | 01 | 70-IG-62-0001 | 400/230V Emergency L & SP DB -Main Gate house - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Gate House | 1600 x 600 x 2000 | Note - 4
28 | 00 | 70-IV-62-0003 | 0.69/0.42kV Emergency L & SP Transformer - CCR - Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | CCR | Part of Lighting Distribution board | Part of Lighting Distribution board
29 | 01 | 70-IG-62-0003 | 400/230V Emergency L & SP DB -Control Building - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | CCR | 1600 x 600 x Note - 2 | Note - 4
30 | 00 | 70-IV-62-0004 | 0.69/0.42kV Emergency L & SP Transformer - Warehouse - Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK2-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Warehouse | Part of Lighting Distribution board | Part of Lighting Distribution board
31 | 01 | 70-IG-62-0004 | 400/230V Emergency L & SP DB -Warehouse - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Warehouse | 1600 x 600 x Note - 2 | Note - 4
32 | 00 | 70-IV-62-0006 | 0.69/0.42kV Emergency L & SP Transformer - Workshop - Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Workshop | Part of Lighting Distribution board | Part of Lighting Distribution board
33 | 01 | 70-IG-62-0006 | 400/230V Emergency L & SP DB -Workshop - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Workshop | 1600 x 600 x Note - 2 | Note - 4
34 | 00 | 70-IV-62-0007 | 0.69/0.42kV Emergency L & SP Transformer - Adminstration Building - Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK2-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Adminstration Building | Part of Lighting Distribution board | Part of Lighting Distribution board
35 | 01 | 70-IG-62-0007 | 400/230V Emergency L & SP DB -Adminstration Building - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Adminstration Building | 1600 x 600 x Note - 2 | Note - 4
36 | 00 | 70-IV-62-0008 | 0.69/0.42kV Emergency L & SP Transformer - Laboratory - Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Laboratory | Part of Lighting Distribution board | Part of Lighting Distribution board
37 | 01 | 70-IG-62-0008 | 400/230V Emergency L & SP DB -Laboratory - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Laboratory | 1600 x 600 x Note - 2 | Note - 4
38 | 00 | 70-IV-62-0009 | 0.69/0.42kV Emergency L & SP Transformer - Main Substation -Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Substation | Part of Lighting Distribution board | Part of Lighting Distribution board
39 | 01 | 70-IG-62-0009 | 400/230V Emergency L & SP DB -Main Substation - Indoor | 250 | _ | A | 0.4 | TNS | GS EP ELE 137 | 250A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 48Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | 1600 x 600 x Note - 2 | Note - 4
40 | 01 | 70-IV-62-0051 | 0.69/0.42kV Emergency L & SP Transformer - Main Substation -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Substation | Part of Lighting Distribution board | Part of Lighting Distribution board
41 | 01 | 70-IG-62-0051 | 400/230V Emergency L & SP DB -Main Substation - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | 1600 x 600 x Note - 2 | Note - 4
42 | 00 | 70-IV-62-0010 | 0.69/0.42kV Emergency L & SP Transformer - Fire Station - Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Fire Station | Part of Lighting Distribution board | Part of Lighting Distribution board
43 | 01 | 70-IG-62-0010 | 400/230V Emergency L & SP DB -Fire Station - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Fire Station | 1600 x 600 x Note - 2 | Note - 4
44 | 00 | 70-IV-62-0011 | 0.69/0.42kV Emergency L & SP Transformer - ITR East - Utilities -Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR East - Utilities | Part of Lighting Distribution board | Part of Lighting Distribution board
45 | 01 | 70-IG-62-0011 | 400/230V Emergency L & SP DB -ITR East-Utilities - Indoor | 250 | _ | A | 0.4 | TNS | GS EP ELE 137 | 250A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 48Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR East - Utilities | 1600 x 600 x Note - 2 | Note - 4
46 | 01 | 70-IV-62-0052 | 0.69/0.42kV Emergency L & SP Transformer - ITR East - Utilities -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR East - Utilities | Part of Lighting Distribution board | Part of Lighting Distribution board
47 | 01 | 70-IG-62-0052 | 400/230V Emergency L & SP DB -ITR East-Utilities - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR East - Utilities | 1600 x 600 x Note - 2 | Note - 4
48 | 00 | 70-IV-62-0012 | 0.69/0.42kV Emergency L & SP Transformer - ITR West - Process -Indoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR West - Process | Part of Lighting Distribution board | Part of Lighting Distribution board
49 | 01 | 70-IG-62-0012 | 400/230V Emergency L & SP DB -ITR West-Process - Indoor | 320 | _ | A | 0.4 | TNS | GS EP ELE 137 | 320A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 48Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR West - Process | 1600 x 600 x Note - 2 | Note - 4
50 | 01 | 70-IV-62-0053 | 0.69/0.42kV Emergency L & SP Transformer - ITR West - Process -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR West - Process | Part of Lighting Distribution board | Part of Lighting Distribution board
51 | 01 | 70-IG-62-0053 | 400/230V Emergency L & SP DB -ITR West-Process - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR West - Process | 1600 x 600 x Note - 2 | Note - 4
52 | 01 | 70-IV-62-0013 | 0.69/0.42kV Emergency L & SP Transformer - Fence Outdoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Fence Outdoor | Part of Lighting Distribution board | Part of Lighting Distribution board
53 | 01 | 70-IG-62-0013 | 400/230V Emergency L & SP DB -Fence Outdoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Fence Outdoor | 1600 x 600 x Note - 2 | Note - 4
54 | 01 | 70-IV-62-0014 | 0.69/0.42kV Emergency L & SP Transformer - Fence Outdoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Fence Outdoor | Part of Lighting Distribution board | Part of Lighting Distribution board
55 | 01 | 70-IG-62-0014 | 400/230V Emergency L & SP DB -Fence Outdoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Fence Outdoor | 1600 x 600 x Note - 2 | Note - 4
56 | 01 | 70-IV-62-0015 | 0.69/0.42kV Emergency L & SP Transformer - Fence Outdoor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Fence Outdoor | Part of Lighting Distribution board | Part of Lighting Distribution board
57 | 01 | 70-IG-62-0015 | 400/230V Emergency L & SP DB -Fence Outdoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Fence Outdoor | 1600 x 600 x Note - 2 | Note - 4
58 | 01 | 70-IV-62-0019 | 0.69/0.42kV Emergency L & SP Transformer - Process Field | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Booster / Flash gas compressor area | Part of Distribution board | Part of Distribution board
59 | 01 | 70-IG-62-0019 | 400/230V Emergency L & SP DB -Process - Field | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Booster / Flash gas compressor area | 1600 x 600 x 2000 | Note - 4
60 | 01 | 70-IV-62-0017 | 0.69/0.42kV MOV Distribution Board Transformer - CPF Outdoor -Booster compressor | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | CPF - Outdoor -Booster compressor | Part of Lighting Distribution board | Part of MOV Distribution board
61 | 01 | 70-IG-62-0017 | MOV Distribution Board - CPF Outdoor - Booster compressor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | CPF - Outdoor -Booster compressor | 1600 x 600 x Note - 2 | Note - 4
62 | 01 | 70-IV-62-0018 | 0.69/0.42kV MOV Distribution Board Transformer - CPF - Outdoor - Slug Catcher | _ | 40 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | CPF - Outdoor -Slug Catcher | Part of Lighting Distribution board | Part of MOV Distribution board
63 | 01 | 70-IG-62-0018 | MOV Distribution Board - CPF -Outdoor - Slug Catcher | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | CPF - Outdoor -Slug Catcher | 1600 x 600 x Note - 2 | Note - 4
64 | 00 | 70-IV-62-0054 | 0.4/0.42kV Normal L & SP Transformer - Main Gate House -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Gate House | Part of Lighting Distribution board | Part of Lighting Distribution board
65 | 00 | 70-IG-62-0054 | 400/230V Normal L & SP DB - Main Gate house - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Gate House | 1600 x 600 x 2000 | Note - 4
66 | 00 | 70-IV-62-0056A | 0.4/0.42kV Normal L & SP Transformer - CCR - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | CCR | Part of Lighting Distribution board | Part of Lighting Distribution board
67 | 01 | 70-IG-62-0056A | 400/230V Normal L & SP DB -Control Building - Indoor A | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | CCR | 1600 x 600 x Note - 2 | Note - 4
68 | 00 | 70-IV-62-0056B | 0.4/0.42kV Normal L & SP Transformer - CCR - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | CCR | Part of Lighting Distribution board | Part of Lighting Distribution board
69 | 01 | 70-IG-62-0056B | 400/230V Normal L & SP DB -Control Building - Indoor B | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | CCR | 1600 x 600 x Note - 2 | Note - 4
70 | 00 | 70-IV-62-0057A | 0.4/0.42kV Normal L & SP Transformer - Warehouse - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Warehouse | Part of Lighting Distribution board | Part of Lighting Distribution board
71 | 01 | 70-IG-62-0057A | 400/230V Normal L & SP DB -Warehouse - Indoor A | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Warehouse | 1600 x 600 x Note - 2 | Note - 4
72 | 00 | 70-IV-62-0057B | 0.4/0.42kV Normal L & SP Transformer - Warehouse - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Warehouse | Part of Lighting Distribution board | Part of Lighting Distribution board
73 | 01 | 70-IG-62-0057B | 400/230V Normal L & SP DB -Warehouse - Indoor B | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Warehouse | 1600 x 600 x Note - 2 | Note - 4
74 | 00 | 70-IV-62-0059A | 0.4/0.42kV Normal L & SP Transformer - Workshop - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Workshop | Part of Lighting Distribution board | Part of Lighting Distribution board
75 | 01 | 70-IG-62-0059A | 400/230V Normal L & SP DB -Workshop - Indoor A | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Workshop | 1600 x 600 x Note - 2 | Note - 4
76 | 00 | 70-IV-62-0059B | 0.4/0.42kV Normal L & SP Transformer - Workshop - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Workshop | Part of Lighting Distribution board | Part of Lighting Distribution board
77 | 01 | 70-IG-62-0059B | 400/230V Normal L & SP DB -Workshop - Indoor B | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Workshop | 1600 x 600 x Note - 2 | Note - 4
78 | 00 | 70-IV-62-0060 | 0.4/0.42kV Normal L & SP Transformer - Adminstration Building - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Adminstration Building | Part of Lighting Distribution board | Part of Lighting Distribution board
79 | 01 | 70-IG-62-0060 | 400/230V Normal L & SP DB -Adminstration Building - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Adminstration Building | 1600 x 600 x Note - 2 | Note - 4
80 | 00 | 70-IV-62-0061 | 0.4/0.42kV Normal L & SP Transformer - Laboratory - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Laboratory | Part of Lighting Distribution board | Part of Lighting Distribution board
81 | 01 | 70-IG-62-0061 | 400/230V Normal L & SP DB -Laboratory - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Laboratory | 1600 x 600 x Note - 2 | Note - 4
82 | 00 | 70-IV-62-0062A | 0.4/0.42kV Normal L & SP Transformer - Main Substation -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Substation | Part of Lighting Distribution board | Part of Lighting Distribution board
83 | 01 | 70-IG-62-0062A | 400/230V Normal L & SP DB - Main Substation - Indoor A | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | 1600 x 600 x Note - 2 | Note - 4
84 | 00 | 70-IV-62-0062B | 0.4/0.42kV Normal L & SP Transformer - Main Substation -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Substation | Part of Lighting Distribution board | Part of Lighting Distribution board
85 | 01 | 70-IG-62-0062B | 400/230V Normal L & SP DB - Main Substation - Indoor B | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | 1600 x 600 x Note - 2 | Note - 4
86 | 00 | 70-IV-62-0063 | 0.4/0.42kV Normal L & SP Transformer - Fire Station - Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Fire Station | Part of Lighting Distribution board | Part of Lighting Distribution board
87 | 00 | 70-IG-62-0063 | 400/230V Normal L & SP DB - Fire Station - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Fire Station | 1600 x 600 x Note - 2 | Note - 4
88 | 00 | 70-IV-62-0064A | 0.4/0.42kV Normal L & SP Transformer - ITR East - Utilities -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR East - Utilities | Part of Lighting Distribution board | Part of Lighting Distribution board
89 | 01 | 70-IG-62-0064A | 400/230V Normal L & SP DB - ITR East-Utilities - Indoor A | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR East - Utilities | 1600 x 600 x Note - 2 | Note - 4
90 | 00 | 70-IV-62-0064B | 0.4/0.42kV Normal L & SP Transformer - ITR East - Utilities -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR East - Utilities | Part of Lighting Distribution board | Part of Lighting Distribution board
91 | 01 | 70-IG-62-0064B | 400/230V Normal L & SP DB - ITR East-Utilities - Indoor B | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR East - Utilities | 1600 x 600 x Note - 2 | Note - 4
92 | 00 | 70-IV-62-0065A | 0.4/0.42kV Normal L & SP Transformer - ITR West - Process -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR West - Process | Part of Lighting Distribution board | Part of Lighting Distribution board
93 | 01 | 70-IG-62-0065A | 400/230V Normal L & SP DB - ITR West-Process - Indoor A | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR West - Process | 1600 x 600 x Note - 2 | Note - 4
94 | 00 | 70-IV-62-0065B | 0.4/0.42kV Normal L & SP Transformer - ITR West - Process -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | ITR West - Process | Part of Lighting Distribution board | Part of Lighting Distribution board
95 | 01 | 70-IG-62-0065B | 400/230V Normal L & SP DB - ITR West-Process - Indoor B | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 24Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR West - Process | 1600 x 600 x Note - 2 | Note - 4
96 | 01 | 70-IV-62-0066 | 0.4/0.42kV Emergency L & SP Transformer - Process Field | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Booster / Flash gas compressor area | Part of Distribution board | Part of Distribution board
97 | 01 | 70-IG-62-0066 | 400/230V Emergency L & SP DB -Process - Field | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Booster / Flash gas compressor area | 1600 x 600 x 2000 | Note - 4
96 | 01 | 70-IV-65-0080 | 0.69/0.42kV Emergency Heat Tracing Transformer - Indoor | _ | 100 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TT | GS EP ELE 142 | 100kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure: Encapsulated cast-resin or Vacuum Pressure impregnated Connection: (Primary (Cable) / Secondary (Cable) CTs & VTs: As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Substation | Part of Distribution board | Part of Distribution board
97 | 01 | 70-IG-65-0080 | 400/230V Emergency Heat Tracing DB - Indoor | 160 | _ | A | 0.4 | TT | GS EP ELE 137 | 160A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | 1600 x 600 x Note - 2 | Note - 4
98 | 01 | 70-IV-65-0081 | 0.69/0.42kV Emergency Heat Tracing Transformer - Outdoor | _ | 100 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TT | GS EP ELE 142 | 100kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Booster and Flash Gas Compressor area | Part of Distribution board | Part of Distribution board
99 | 01 | 70-IG-65-0081 | 400/230V Emergency Heat Tracing DB - Outdoor | 160 | _ | A | 0.4 | TT | GS EP ELE 137 | 160A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Booster and Flash Gas Compressor area | 1600 x 600 x 2000 | Note - 4
100 | 01 | 70-IV-65-0082 | 0.69/0.42kV Emergency Heat Tracing Transformer - Outdoor | _ | 100 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TT | GS EP ELE 142 | 100kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Slug Catcher Vapour recovery area | Part of Distribution board | Part of Distribution board
101 | 01 | 70-IG-65-0082 | 400/230V Emergency Heat Tracing -Outdoor | 160 | _ | A | 0.4 | TT | GS EP ELE 137 | 160A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Slug Catcher Vapour recovery area | 1600 x 600 x 2000 | Note - 4
102 | 01 | 70-IV-65-0083 | 0.69/0.42kV Emergency Heat Tracing Transformer - Outdoor | _ | 100 | kVA | 0.69 | Primary: IT (fault limited to 150mA) Secondary:TT | GS EP ELE 142 | 100kVA, 0.69/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Chemical & Utilities area | Part of Distribution board | Part of Distribution board
103 | 01 | 70-IG-65-0083 | 400/230V Emergency Heat Tracing -Outdoor | 160 | _ | A | 0.4 | TT | GS EP ELE 137 | 160A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Chemical & Utilities area | 1600 x 600 x 2000 | Note - 4
104 | 01 | 70-IV-65-0084 | 0.69/0.42kV Heat Tracing Transformer - Outdoor | _ | 100 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TT | GS EP ELE 142 | 100kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Booster and Flash Gas Compressor area | Part of Distribution board | Part of Distribution board
105 | 01 | 70-IG-65-0084 | 400/230V Heat Tracing - Outdoor | 160 | _ | A | 0.4 | TT | GS EP ELE 137 | 160A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Booster and Flash Gas Compressor area | 1600 x 600 x 2000 | Note - 4
106 | 01 | 70-IV-65-0085 | 0.4/0.42kV Heat Tracing Transformer - Outdoor | _ | 100 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TT | GS EP ELE 142 | 100kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Equipment type of protection : Ex "db", IP:55 Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Slug Catcher Vapour recovery area | Part of Distribution board | Part of Distribution board
107 | 01 | 70-IG-65-0085 | 400/230V Heat Tracing - Outdoor | 160 | _ | A | 0.4 | TT | GS EP ELE 137 | 160A, 50Hz, 10kA for 1 sec | Equipment type of protection : Ex "db", IP:55 Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Slug Catcher Vapour recovery area | 1600 x 600 x 2000 | Note - 4
108 | 01 | Note 11 | Electrical control system Panel A / B-Main Substation | _ | _ | _ | 0.23 | _ | GS EP ELE 221 | _ | _ | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Main Substation | Panel A 800 X 800 X 2000 Panel B 800 X 800 X 2000 | Note - 4 | Note 11
109 | 01 | Note 11 | Electrical control system Panel A / B-CCR | _ | _ | _ | 0.23 | _ | GS EP ELE 221 | _ | _ | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | CCR | Panel A 800 X 800 X 2000 Panel B 800 X 800 X 2000 | Note - 4 | Note 11
110 | 01 | Note 11 | Electrical control system Panel A/B - Process ITR | _ | _ | _ | 0.23 | _ | GS EP ELE 221 | _ | _ | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Process ITR | Panel A 800 X 800 X 2000 Panel B 800 X 800 X 2000 | Note - 4 | Note 11
111 | 01 | Note 11 | Electrical control system Panel A/B - Utility ITR | _ | _ | _ | 0.23 | _ | GS EP ELE 221 | _ | _ | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Utility ITR | Panel A 800 X 800 X 2000 Panel B 800 X 800 X 2000 | Note - 4 | Note 11
112 | 01 | 70-GU-06-0001A | 110V DC UPS A System | _ | 5 | kW | 0.11 | Unearthed (associated with insulation monitoring) | GS EP ELE 151 | 5kW, 100A with Ni-Cd battery bank, autonomy time 30 minutes. | Industrial Type DC UPS: Configuration: 2B-Redundant DC UPS with separate battery (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 151 - DC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | DC UPS 800 x 800 x 2500 Battery 2500 x 800 x 1500 | Note - 4 | Note - 6
113 | 01 | 70-GU-06-0001B | 110V DC UPS B System | _ | 5 | kW | 0.11 | Unearthed (associated with insulation monitoring) | GS EP ELE 151 | 5kW, 100A with Ni-Cd battery bank, autonomy time 30 minutes. | Industrial Type DC UPS: Configuration: 2B-Redundant DC UPS with separate battery (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 151 - DC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | DC UPS 800 x 800 x 2500 Battery 2500 x 800 x 1500 | Note - 4 | Note - 6
114 | 01 | 70-GU-06-0002A / B | 230V AC UPS A/B in Main Substation for Telecomms | _ | 10 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 10kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 100% load | Modular Type AC UPS: Configuration: 3b- AC UPS without External By-pass cabinet (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Main Substation | UPS A&B - 2000 x 800 x 2200 Battery A - 2500 x 800 x 1500 Battery B - 2500 x 800 x 1500 | Note - 4 | Note - 6
115 | 01 | 70-GU-06-0003A / B | 230V AC UPS A/B in Process - ITR for Telecomms | _ | 10 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 10kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 100% load | Industrial Type AC UPS: Configuration: 3D(ii)- Redundant AC UPS with common Bypass - 3 Bus distribution panel (with ATS for single input loads) (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR West - Process | UPS A&B - 2000 x 800 x 2200 Battery A - 2500 x 800 x 1500 Battery B - 2500 x 800 x 1500 | Note - 4
116 | 02 | 70-GU-06-0004A / B | 230V AC UPS A/B in Process - ITR for Instruments | _ | 50 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 50kVA, with Ni-Cd battery bank, autonomy time 30 minutes. Note : Each battery bank A / B - each sized for 100% load | Industrial Type AC UPS: Configuration: 3D(ii)- Redundant AC UPS with common Bypass - 3 Bus distribution panel (with ATS for single input loads) (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR West - Process | UPS A&B - 5600 x 800 x 2200 Battery A - 5000 x 2200 x 2200 Battery B - 5000 x 2200 x 2200 Battery Isolator A - 600 x 400 x 1000 Battery Isolator B - 600 x 400 x 1000 | Note - 4
117 | 01 | 70-GU-06-0005A / B | 230V AC UPS A/B in Utility - ITR for Telecomms | _ | 10 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 10kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 100% load | Industrial Type AC UPS: Configuration: 3D(ii)- Redundant AC UPS with common Bypass - 3 Bus distribution panel (with ATS for single input loads) (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR East - Utilities | UPS A&B - 2000 x 800 x 2200 Battery A - 2500 x 800 x 1500 Battery B - 2500 x 800 x 1500 | Note - 4
118 | 01 | 70-GU-06-0006A / B | 230V AC UPS A/B in Utility - ITR for Instruments | _ | 50 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 50kVA, with Ni-Cd battery bank, autonomy time 30 minutes. Note : Each battery bank A / B - each sized for 100% load | Industrial Type AC UPS: Configuration: 3D(ii)- Redundant AC UPS with common Bypass - 3 Bus distribution panel (with ATS for single input loads) (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | ITR East - Utilities | UPS A&B - 5600 x 800 x 2200 Battery A - 5000 x 1500 x 1500 Battery B - 5000 x 1500 x 1500 Battery Isolator A - 600 x 400 x 1000 Battery Isolator B - 600 x 400 x 1000 | Note - 4
119 | 01 | 70-GU-06-0007A / B | 230V AC UPS A/B in Control Building for Telecomms | _ | 60 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 60kVA, with Ni-Cd battery bank, autonomy time 30 minutes. Note : Each battery bank A / B - each sized for 100% load | Industrial Type AC UPS: Configuration: 3D(ii)- Redundant AC UPS with common Bypass - 3 Bus distribution panel (with ATS for single input loads) (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | CCR | UPS A&B - 5600 x 800 x 2200 Battery A - 5000 x 2200 x 2200 Battery B - 5000 x 2200 x 2200 Battery Isolator A - 600 x 400 x 1000 Battery Isolator B - 600 x 400 x 1000 | Note - 4
120 | 02 | 70-GU-06-0008A / B | 230V AC UPS A/B in Control Building for Instruments | _ | 70 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 70kVA, with Ni-Cd battery bank, autonomy time 30 minutes. Note : Each battery bank A / B - each sized for 100% load | Industrial Type AC UPS: Configuration: 3D(ii)- Redundant AC UPS with common Bypass - 3 Bus distribution panel (with ATS for single input loads) (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | CCR | UPS A&B - 5600 x 800 x 2200 Battery A - 5000 x 2200 x 2200 Battery B - 5000 x 2200 x 2200 Battery Isolator A - 600 x 400 x 1000 Battery Isolator B - 600 x 400 x 1000 | Note - 4
121 | 01 | 70-GU-06-0009A / B | 230V AC UPS A/B in Warehouse for Telecoms | _ | 10 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 10kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 100% load | Modular Type AC UPS: Configuration: 3b- AC UPS without External By-pass cabinet (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Warehouse | UPS A&B - 2000 x 800 x 2200 Battery A - 2500 x 800 x 1500 Battery B - 2500 x 800 x 1500 | Note - 4
122 | 01 | 70-GU-06-0010A / B | 230V AC UPS A/B in Workshop for Telecoms | _ | 10 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 10kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 100% load | Modular Type AC UPS: Configuration: 3b- AC UPS without External By-pass cabinet (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Workshop | UPS A&B - 2000 x 800 x 2200 Battery A - 2500 x 800 x 1500 Battery B - 2500 x 800 x 1500 | Note - 4
123 | 01 | 70-GU-06-0011A / B | 230V AC UPS A/B in Adminstration Building for Telecoms | _ | 40 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 40kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 100% load | Industrial Type AC UPS: Configuration: 3D(ii)- Redundant AC UPS with common Bypass - 3 Bus distribution panel (with ATS for single input loads) (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Adminstration Building | UPS A&B - 5600 x 800 x 2200 Battery A - 5000 x 1500 x 1500 Battery B - 5000 x 1500 x 1500 Battery Isolator A - 600 x 400 x 1000 Battery Isolator B - 600 x 400 x 1000 | Note - 4
124 | 01 | 70-GU-06-0013A / B | 230V AC UPS A/B in Fire Station for Telecoms | _ | 10 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 10kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 100% load | Modular Type AC UPS: Configuration: 3b- AC UPS without External By-pass cabinet (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162701 - Single Line Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162001 - Substation Equipment layout | Fire Station | UPS A&B - 2000 x 800 x 2200 Battery A - 2500 x 800 x 1500 Battery B - 2500 x 800 x 1500 | Note - 4
1 | 01 | 81-IV-61-0001 | Beach Valve Substation LV 11/0.42kV Emergency Transformer | _ | 100 | kVA | 11 | Primary: Resistance earthed (20-50A) Secondary:IT (High Impedance earthed) Impedance limiting earth fault to 150 mA. | GS EP ELE 142 | 100kVA, 11/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 141 - Dry-Type transformer AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-81-SK02-162702 - Single Line Diagrams - Beach Valve Station AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Beach Valve Station | 1000 x 800 x 1500 | Note - 4
2 | 00 | 81-IRR-61-0001 | Neutral Earthing Resistor for transformer 81-IV-61-0003 | 150 | _ | mA | 0.4 | IT (Impedance limiting earth fault to 150 mA and surge arrester) Refer Note - 10 | GS EP ELE 190 | 0.4kV, 150mA | Enclosure : Part of Switchgear Connection : Part of Switchgear CTs : As per Typical Protection & Specs of main equipment. | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 190 - Neutral Earthing Resistor AZ-AB1-81-SK02-162702 - Single Line Diagrams - Beach Valve Station AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-162005 - Electrical Room Equipment and Power Layout Beach Valve Station | Beach Valve Station | Part of Switchgear | Part of Switchgear
3 | 01 | 81-IK-61-0001 | Beach Valve Station 400V Emergency Switchgear | 630 | _ | A | 0.4 | IT (High Impedance earthed) Impedance limiting earth fault to 150 mA. | GS EP ELE 135 | 630A, 50Hz, 25kA for 1 sec. | Insulation type : Air Arcing Class B Equipped with Electrical and Mechanical Interlocks Communication Protocol: Modbus + IEC 61850 Protection: As per P&M diagrams Circuit details: Incomer - 1 nos Bus - tie - No Outgoing feeders - Refer to Doc. No.AZ-AB1-70-SK02-160008 - Electrical Load List | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 135 - Low Voltage Switchgear and controlgear assemblies according to IOGP S-560 AZ-AB1-81-SK02-162702 - Single Line Diagrams - Beach Valve Station AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162005 - Electrical Room Equipment and Power Layout Beach Valve Station AZ-AB1-70-SK02-162007 - Typical Protection Diagrams | Beach Valve Station | 2400 x 1000 x 2200 | Note - 4
4 | 00 | 81-IV-62-0001 | 0.4/0.42kV Emergency L & SP Transformer - Beach Valve Station -Indoor | _ | 40 | kVA | 0.4 | Primary: IT (fault limited to 150mA) Secondary:TNS | GS EP ELE 142 | 40kVA, 0.4/0.42kV, Dyn11, AN, Dry type Transformer, DETC +/- 5%(Steps of +/- 2.5), Z= 4% | Enclosure : Encapsulated cast-resin or Vacuum Pressure impregnated Connection : (Primary (Cable) / Secondary (Cable) CTs & VTs : As per Typical Protection & Specs of main equipment. Protections: As per Typical Protection & Specs of main equipment. Equipped with Electrical and Mechanical Interlocks | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 142 - Dry-Type transformer AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Beach Valve Station | Part of Lighting Distribution board | Part of Lighting Distribution board
5 | 00 | 81-IG-62-0001 | 400/230V Emergency L & SP DB -Beach Valve ITR - Indoor | 63 | _ | A | 0.4 | TNS | GS EP ELE 137 | 63A, 50Hz, 10kA for 1 sec | Connection: (Incomer (Cable) / Outgoing (Cable)) Protections: As per Typical Protection & Specs of main equipment. No of ways / configuration. 36Way . | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 137 - Distribution boards AZ-AB1-81-SK02-162702 - Single Line Diagrams - Beach Valve Station AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162005 - Electrical Room Equipment and Power Layout Beach Valve Station | Beach Valve Station | 1600 x 600 x 2000 | Note - 4
6 | 00 | 81-GU-06-0001A / B | 230V AC UPS A/B in Beach valve Station for Telecoms | _ | 5 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 5kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 50% load |  | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162702 - Single Line Diagrams - Beach Valve Station AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162005 - Electrical Room Equipment and Power Layout Beach Valve Station | Beach Valve Station | UPS A&B - 2200 x 800 x 2200 Battery A - 2000 x 1000 x 1500 Battery B - 2000 x 1000 x 1500 | Note - 4
7 | 00 | 81-GU-06-0002A / B | 230V AC UPS A/B in Beach valve Station for Instruments | _ | 5 | kVA | 0.23 | Isolated IT System | GS EP ELE 152 | 5kVA, with Ni-Cd battery bank, autonomy time 2 Hours. Note : Each battery bank A / B - each sized for 50% load | Modular Type AC UPS: Configuration: 3b- AC UPS without External By-pass cabinet (as per spec) | GS EP ELE 001 - Electrical Design Criteria GS EP ELE 152 - AC Uninterruptible Power Systems (UPS) AZ-AB1-70-SK02-162702 - Single Line Diagrams - Beach Valve Station AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipment AZ-AB1-70-SK02-160018 - Power System Study AZ-AB1-70-SK02-160008 - Electrical Load List AZ-AB1-70-SK02-162005 - Electrical Room Equipment and Power Layout Beach Valve Station | Beach Valve Station | UPS A&B - 2200 x 800 x 2200 Battery A - 2000 x 1000 x 1500 Battery B - 2000 x 1000 x 1500 | Note - 4
8 | 01 | Note 11 | Electrical control system Panel A/B - Beach Valve station | _ | _ | _ | 0.23 | _ | GS EP ELE 221 | _ | _ | AZ-AB1-70-SK02-162007 - Typical Protection Diagrams AZ-AB1-70-SK02-160001 - Electrical Basis of Design AZ-AB1-70-SK02-161000 - Typical Logic Diagrams AZ-AB1-70-SK02-160011 - Electrical I/O List for Electrical Control System (ECS) AZ-AB1-70-SK02-160012 - Electrical I/O List for ICSS AZ-AB1-70-SK02-160016 - Cable Schedule AZ-AB1-70-SK02-160002 - Specifications of Main Electrical Equipments | Beach Valve Station | Panel A 800 X 800 X 2000 Panel B 800 X 800 X 2000 | Note - 4 | Note 11

## Sheet2
BOM DESCRIPTION | UNIT | QUANTITY AS PER ITB | QUANTITY SPARE | QUANTITY ADDED AS ASSUMED | TOTAL QTY | WIDTH/FEEDER | TOTAL WIDTH | PANEL QTY |  | CODE
1.0 Active Feeders
11kV SWGR-1001
Incoming Bus A | PNL | 1 |  |  | 1 | 1000 | 1000 | 1
Incoming Bus B | PNL | 1 |  |  | 1 | 1000 | 1000 | 1
Bus Tie | PNL | 1 |  |  | 1 | 1000 | 1000 | 1
PT Panel | PNL |  |  |  | 2 | 650 | 1300 | 2
11kV Steam Turbine Generator Incomer Cubicle | PNL | 1 |  |  | 1 | 1000 | 1000 | 1
11kV Transformer Feeder Cubicle (per Dwg MV1) | PNL | 8 |  |  | 8 | 800 | 6400 | 8
11kV Spare Feeder Cubicle | PNL | 0 | 2 |  | 2 | 800 | 1600 | 2
DUMMY PANEL |  |  |  |  | 4 | 400 | 1600 | 4
[7 empty] | 14900 | 20
6.6kV SWGR-2001
Incoming Bus A | PNL | 1 |  |  | 1 | 1000 | 1000 | 1
Incoming Bus B | PNL | 1 |  |  | 1 | 1000 | 1000 | 1
Bus Tie | PNL | 1 |  |  | 1 | 1000 | 1000 | 1
PT Panel | PNL |  |  |  | 2 | 650 | 1300 | 2
6.6kV FVNR Motor Starter Cubicle (P ≤ 1MW, per Dwg MV2) - VCU | PNL | 10 |  |  | 10 | 800 | 8000 | 10
6.6kV FVNR Motor Starter Cubicle (P > 1MW, per Dwg MV3) - VCB | PNL | 1 |  |  | 1 | 800 | 800 | 1
6.6kV VSD Motor Feeder Cubicle (per Dwg MV4) | PNL | 2 |  |  | 2 | 800 | 1600 | 2
6.6kV Spare Feeder Cubicle
6.6kV FVNR Motor Starter Cubicle (P ≤ 1MW, per Dwg MV2) - VCU | PNL |  | 2 |  | 2 | 800 | 1600 | 2
6.6kV FVNR Motor Starter Cubicle (P > 1MW, per Dwg MV3) - VCB | PNL |  | 1 |  | 1 | 800 | 800 | 1
6.6kV VSD Motor Feeder Cubicle (per Dwg MV4) | PNL |  | 1 |  | 1 | 800 | 800 | 1
DUMMY PANEL |  |  |  |  | 4 | 400 | 1600 | 4
[7 empty] | 19500 | 26
PMCC-3001 A
PMCC-3001 Bus A
Incoming Bus A | PNL | 1 | 0 |  | 1 | 600 | 600 | 1 | Incoming Bus A: 1 PNL | INCOMING BUS A
Bus Tie | PNL | 1 | 0 |  | 1 | 600 | 600 | 1 | Bus Tie: 1 PNL | BUS TIE
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | 9 | 3 | 0 | 12 | 600 | 7200 | 12 | 400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1): 12 PNL | ACB
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2): 1 EACH | MCCB_1
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | 16 | 5 | 0 | 21 | 600 | 12600 | 21 | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3): 21 EACH | MCCB_2
400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10) | EACH | 11 | 4 | 0 | 15 | 600 | 9000 | 15 | 400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10): 15 EACH | MOTOR_STARTER
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | 29 | 9 | 0 | 38 | 600 |  |  | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4): 38 EACH | MCC_B2B
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5): 1 EACH | MCC_B2B
400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | EACH | 5 | 2 | 0 | 7 | 600 |  |  | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8): 7 EACH | MCC_B2B
400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | EACH | 9 | 3 | 0 | 12 | 600 |  |  | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9): 12 EACH | MCC_B2B
400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11) | EACH | 0 | 0 | 1 | 1 | 600 | 2400 | 4 | 400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11): 1 EACH | MCC_B2B
PMCC-3001 Bus B
Incoming Bus B | PNL | 1 | 0 |  | 1 | 600 | 600 | 1 | Incoming Bus B: 1 PNL | INCOMING BUS B
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | 9 | 2 | 0 | 11 | 600 | 6600 | 11 | 400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1): 11 PNL | ACB
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2): 1 EACH | MCCB_1
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | 16 | 4 | 0 | 20 | 600 | 12000 | 20 | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3): 20 EACH | MCCB_2
400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10) | EACH | 11 | 3 | 0 | 14 | 600 | 8400 | 14 | 400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10): 14 EACH | MOTOR_STARTER
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | 29 | 6 | 0 | 35 | 600 |  |  | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4): 35 EACH | MCC_B2B
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5): 1 EACH | MCC_B2B
400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | EACH | 5 | 1 | 0 | 6 | 600 |  |  | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8): 6 EACH | MCC_B2B
400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | EACH | 9 | 2 | 0 | 11 | 600 |  |  | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9): 11 EACH | MCC_B2B
400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11) | EACH | 0 | 0 | 1 | 1 | 600 | 2400 | 4 | 400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11): 1 EACH | MCC_B2B
[7 empty] | 63600 | 106
EPMCC-3002 Bus A
Incoming Bus A | PNL | 1 | 0 |  | 1 | 600 | 600 | 1 | Incoming Bus A: 1 PNL | INCOMING BUS A
Bus Tie | PNL | 1 | 0 |  | 1 | 600 | 600 | 1 | Bus Tie: 1 PNL | BUS TIE
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | ACB
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2): 1 EACH | MCCB_1
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MCCB_2
400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MOTOR_STARTER
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V FVNR Motor Starter Cubicles (P ≤ 55kW) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MCC_B2B
EPMCC-3002 Bus B | [8 empty] | EPMCC-3002 Bus B:
Incoming Bus B | PNL | 1 | 0 | 0 | 1 | 600 | 600 | 1 | Incoming Bus B: 1 PNL | INCOMING BUS B
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | ACB
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2): 1 EACH | MCCB_1
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MCCB_2
400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MOTOR_STARTER
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V FVNR Motor Starter Cubicles (P ≤ 55kW) | EACH | #REF! | 0 | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MCC_B2B
EPMCC-3002 Bus C | [8 empty] | EPMCC-3002 Bus C:
EDG Incomer | PNL | 1 | 0 | 0 | 1 | 600 | 600 | 1 | EDG Incomer: 1 PNL | EDG INCOMING
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | EDG TIE
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2): 1 EACH | MCCB_1
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MCCB_2
400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MOTOR_STARTER
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF! | MCC_B2B
400V FVNR Motor Starter Cubicles (P ≤ 55kW) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! | #REF! | #REF! | MCC_B2B
[7 empty] | #REF! | #REF!
PMCC-3003 A
PMCC-3003 Bus A
Incoming Bus A | PNL | 1 | 0 | 0 | 1 | 600 | 600 | 1 | Incoming Bus A: 1 PNL | INCOMING BUS A
Bus Tie | PNL | 1 | 0 | 0 | 1 | 600 | 600 | 1 | Bus Tie: 1 PNL | BUS TIE
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1): 1 PNL | ACB
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2): 1 EACH | MCCB_1
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3): 1 EACH | MCCB_2
400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10): 1 EACH | MOTOR_STARTER
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4): 1 EACH | MCC_B2B
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5): 1 EACH | MCC_B2B
400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8): 1 EACH | MCC_B2B
400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9): 1 EACH | MCC_B2B
400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11): 1 EACH | MCC_B2B
PMCC-3003 Bus B
Incoming Bus B | PNL | 1 | 0 |  | 1 | 600 | 600 | 1 | Incoming Bus B: 1 PNL | INCOMING BUS B
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1): 1 PNL | ACB
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2): 1 EACH | MCCB_1
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3): 1 EACH | MCCB_2
400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V FVNR Motor Starter Cubicle (55kW < P < 200kW, per Dwg LV10): 1 EACH | MOTOR_STARTER
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4): 1 EACH | MCC_B2B
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5): 1 EACH | MCC_B2B
400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8): 1 EACH | MCC_B2B
400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | EACH | 0 | 0 | 1 | 1 | 600 |  |  | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9): 1 EACH | MCC_B2B
400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11) | EACH | 0 | 0 | 1 | 1 | 600 | 600 | 1 | 400V FVNR Motor Starter Cubicle (P ≤ 55kW, per Dwg LV11): 1 EACH | MCC_B2B
[7 empty] | 7800 | 13
SB-7730 A
Incoming Bus A | PNL | 1 | 0 | 0 | 1 | 600 | 600 |  | Incoming Bus A: 1 PNL
Bus Tie | PNL | 1 | 0 | 0 | 1 | 600 | 600 |  | Bus Tie: 1 PNL
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF!
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
SB-7730 B
Incoming Bus B | PNL | 1 | 0 | 0 | 1 | 600 | 600 |  | Incoming Bus B: 1 PNL
400V Air Circuit Breaker (ACB) Feeder Cubicle (per Dwg LV1) | PNL | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
400V MCCB Feeder Cubicle (I > 160A WITHOUT EARTH FAULT, per Dwg LV2) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | EACH | #REF! | #REF! | #REF! | #REF! | 600 |  |  | #REF!
400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | EACH | #REF! | #REF! | #REF! | #REF! | 600 | #REF! |  | #REF!
#REF!
|  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
|  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
|  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
|  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
|  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E
|  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
|  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
|  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 12E
|  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E
|  |  | M-B1 | 400V DOL Motor Starter Cubicle | 12E
|  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E

## Sheet3
F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E
U | 400V UPS Feeder Cubicle | 8E/4
U | 400V UPS Feeder Cubicle | 12E
U | 400V UPS Feeder Cubicle | 8E
F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E
F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E
F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E
F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
M-E1 | 400V DOL Motor Starter Cubicle | 24E
M-B1 | 400V DOL Motor Starter Cubicle | 8E/2
M-A1 | 400V DOL Motor Starter Cubicle | 8E/4

## NOTES
Spares: A 10–20% spare is common in early design. Put or in to apply globally.0.100.20SparePct
Incomers / Bus‑tie: If your ACB incomers and couplers are already rows in the table (e.g., assigned ), they’re already counted. No extra adders needed.72E
Capacity reference: 1 E = 25 mm and 72 E per column face are standard ABB MNS modular dimensions. For back‑to‑back, use 144 E per section footprint (two faces).
|  | M-A1 | 4
|  | M-A1 | 30
|  | M-A1 | 18.6
|  | M-A1 | 5.5
|  | M-A1 | 7.5
|  | M-A1 | 1
|  | M-A1 | 3
|  | M-A1 | 11
|  | M-A1 | 15
|  | M-A1 | 2.2
|  | Motor Rating (kW) @ 400V | Max Current (A) | Module Size | Height (mm) | Type / Density | Notes
|  | :--- | :--- | :--- | :--- | :--- | :---
| M_A1 | **0.37 – 15 kW** | ~32 A | **8E / 4** | 200 mm | **Quarter Module** | 4 modules fit side-by-side in one 600mm width. Maximize density (up to 32+ per col).
| M_A1, M_B1(22kW ~ 37kW) | **18.5 – 37 kW** | ~75 A | **8E / 2** | 200 mm | **Half Module** | 2 modules fit side-by-side. Good for mid-range motors.
| M_B1 | **45 – 75 kW** | ~140 A | **8E** | 200 mm | **Full Width** | Occupies full 600mm width. Requires more cooling/space for breaker.
| M_B1(<=110kW),M_C1 (<132kW) | **90 – 132 kW** | ~250 A | **12E** | 300 mm | Full Width | Larger contactor and thermal dissipation area required.
| M_D1 (110kW ~ 200kW) | **160 – 200 kW** | ~400 A | **16E** | 400 mm | Full Width | Heavy duty. Often the limit for standard "drawer" types.
| M_E1 | **220 – 250 kW** | ~500 A | **24E** | 600 mm | Full Width | Very large withdrawable unit or fixed plug-in design.
|  | **> 250 kW** | > 500 A | **Full Height** | 1800+ mm | Vertical Section | Typically requires a dedicated vertical panel (Air Circuit Breaker or Soft Starter size).
| M_A1(<22kW) | 8E
| M_A1, M_B1(22kW ~ 37kW) | 8E
| M_B1 | 8E
| M_B1(<=110kW),M_C1 (<132kW) | 12E
| M_D1 (110kW ~ 200kW) | 16E
| M_E1 | 24E
mid="AHU", "M-E1",
AND(kw>=0.37, kw<=15), "M-A1",
AND(kw>=18.5, kw<22), "M-A1",
AND(kw>=22, kw<=37), "M-B1",
AND(kw>=45, kw<=75), "M-B1",
AND(kw>=90, kw<=110), "M-B1",
AND(kw>110, kw<132), "M-C1",
AND(kw>=132, kw<=200), "M-D1",
kw>200, "M-E1",
TRUE, "<review
| Module size | Number of poles | I [A] | Max. number of cables and cross section per phase [mm2] | Max. tightening torque [Nm]
| 80000 | 3 | 45 | 1 x 16
| 80000 | 4 | 45 | 1 x 16
| 800 | 3 | 63 | 1 x 35
| 800 | 4 | 63 | 1 x 35
| 800 | 6 | 63 | 1 x 16
| 4E | 3 | 63 | 1 x 25
| 6E | 3 | 250 | 2 x 120 (M10x30) | 45
| >= 8E | 3 | 160 | 2 x 120 (M10x30) | 45
| >= 8E | 3 | 400 | 2 x 240 (M12x35) | 80
| >= 12E | 3 | 630 | 2 x 240 (M12x35) | 80
| >= 8E | 4 | 250 | 2 x 120 (M10x30) | 45
| >= 16E | 4 | 400 | 2 x 240 (M12x35) | 80
| >= 24E | 4 | 630 | 2 x 240 (M12x35) | 80

## ECS_IO_LIST
Equipment Type | CKT TYPE | Unit | SDO | SDI | DO | DI | SAO | SAI | AI | AO | QTY |  | SDO | SDI | DO | DI | SAO | SAI | AI | AO
11kV Switchgear Incomer | INC_11kV | ECS | 0 | 15 | 2 | 7 | 0 | 7 | 2 | 0 | 2 |  | 0 | 30 | 4 | 14 | 0 | 14 | 4 | 0
11kV Bus Tie Breaker | TIE_11kV | ECS | 0 | 18 | 2 | 9 | 0 | 9 | 0 | 0 | 1 |  | 0 | 18 | 2 | 9 | 0 | 9 | 0 | 0
11kV Emergency Diesel Generator Incomer Feeder | GEN_TIE | ECS | 0 | 12 | 2 | 4 | 7 | 0 | 0 | 0 | 1 |  | 0 | 12 | 2 | 4 | 7 | 0 | 0 | 0
11kV Emergency Diesel Generator Package | EDG | ECS | 0 | 23 | 9 | 18 | 0 | 0 | 0 | 0 | 1 |  | 0 | 23 | 9 | 18 | 0 | 0 | 0 | 0
11kV Switchgear Outgoing Transformer Feeder | TR | ECS | 0 | 21 | 3 | 2 | 0 | 9 | 6 | 0 | 9 |  | 0 | 189 | 27 | 18 | 0 | 81 | 54 | 0
11kV Switchgear Outgoing Power Feeder | FDR_11kV | ECS | 0 | 15 | 2 | 2 | 0 | 9 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11kV Switchgear VSD Outgoing Power Feeder | VSD_11kV | ECS | 0 | 14 | 3 | 4 | 0 | 9 | 0 | 0 | 2 |  | 0 | 28 | 6 | 8 | 0 | 18 | 0 | 0
11kV DOL Starter Motor Feeder | DOL_11kV | ECS | 0 | 23 | 3 | 3 | 0 | 9 | 0 | 0 | 4 |  | 0 | 92 | 12 | 12 | 0 | 36 | 0 | 0
690V Switchgear Incomer | INC_LV | ECS | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0 | 5 |  | 0 | 60 | 10 | 30 | 0 | 45 | 0 | 0
400V Switchgear Incomer | INC_LV | ECS | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0 | 10 |  | 0 | 120 | 20 | 60 | 0 | 90 | 0 | 0
690V Bus Tie Breaker | TIE_LV | ECS | 0 | 14 | 2 | 11 | 0 | 9 | 0 | 0 | 3 |  | 0 | 42 | 6 | 33 | 0 | 27 | 0 | 0
400V Bus Tie Breaker | TIE_LV | ECS | 0 | 14 | 2 | 11 | 0 | 9 | 0 | 0 | 1 |  | 0 | 14 | 2 | 11 | 0 | 9 | 0 | 0
690V Switchgear Emergency Switchgear Incomer Feeder | INC_LV_EM | ECS | 0 | 13 | 2 | 7 | 0 | 6 | 0 | 0 | 1 |  | 0 | 13 | 2 | 7 | 0 | 6 | 0 | 0
690V Heater Panel Feeder | H1_LV | ECS | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
690V Heater and Thyristor Control Panel Feeder | H2_LV | ECS | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 18 |  | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0
690V DOL Starter (Types D1 & E1) | DOL_LV | ECS | 0 | 10 | 0 | 2 | 0 | 0 | 0 | 0 | 7 |  | 0 | 70 | 0 | 14 | 0 | 0 | 0 | 0
690V / 400V Switchgear Panel with VSD | VSD_LV | ECS | 0 | 10 | 0 | 3 | 0 | 0 | 0 | 0 | 4 |  | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0
690V / 400V Soft Starter | VSD_LV | ECS | 0 | 10 | 0 | 3 | 0 | 0 | 0 | 0 | 4 |  | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0
400V DOL Starter (Type C1) | DOL_C1_LV | ECS | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC UPS System | AC_UPS | ECS | 0 | 19 | 0 | 6 | 0 | 5 | 0 | 0 | 11 |  | 0 | 209 | 0 | 66 | 0 | 55 | 0 | 0
DC UPS System | DC_UPS | ECS | 0 | 12 | 0 | 5 | 0 | 4 | 0 | 0 | 1 |  | 0 | 12 | 0 | 5 | 0 | 4 | 0 | 0
Distribution Boards and Sub-Distribution Boards | DB | ECS | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 46 |  | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0
HVAC Control Panel Interface with ECS | HVAC | ECS | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 8 |  | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0
ICSS Interface | ICSS | ECS | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 0
[13 empty] | 3 | 1054 | 102 | 387 | 8 | 395 | 58 | 0
[12 empty] | SPARE (30%) | 4 | 1371 | 133 | 504 | 11 | 514 | 76 | 0
[12 empty] | TOTAL FROM BREAKDOWN | 4 | 1371 | 133 | 504 | 11 | 514 | 76 | 0
[12 empty] | DIFF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | SDO | SDI | DO | DI | SAO | SAI | AI | AO
[13 empty] | 10 | 1400 | 150 | 600 | 20 | 520 | 100 | 10
[13 empty] | 10 | 1400 | 150 | 600 | 20 | 520 | 100 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10
LOCATION: ITR PROCESS | [12 empty] | SDO: TOTAL
Equipment Type | CKT TYPE | Unit | SDO | SDI | DO | DI | SAO | SAI | AI | AO | QTY |  | SDO | SDI | DO | DI | SAO | SAI | AI | AO
400V Switchgear Incomer (HVAC MCC) | INC_LV | ECS | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0 | 1 |  | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0
Distribution Boards and Sub-Distribution Boards | DB | ECS | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5 |  | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0
AC UPS System | AC_UPS | ECS | 0 | 19 | 0 | 6 | 0 | 5 | 0 | 0 | 2 |  | 0 | 38 | 0 | 12 | 0 | 10 | 0 | 0
[13 empty] | 0 | 116 | 9 | 53 | 0 | 39 | 0 | 0
[13 empty] | 0 | 120 | 10 | 90 | 0 | 40 | 0 | 0
LOCATION: ITR UTILITY
Equipment Type | CKT TYPE | Unit | SDO | SDI | DO | DI | SAO | SAI | AI | AO | QTY |  | SDO | SDI | DO | DI | SAO | SAI | AI | AO
400V Switchgear Incomer (HVAC MCC) | INC_LV | ECS | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0 | 1 |  | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0
Distribution Boards and Sub-Distribution Boards | DB | ECS | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 5 |  | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0
AC UPS System | AC_UPS | ECS | 0 | 19 | 0 | 6 | 0 | 5 | 0 | 0 | 2 |  | 0 | 38 | 0 | 12 | 0 | 10 | 0 | 0
[13 empty] | 0 | 116 | 6 | 53 | 0 | 39 | 0 | 0
[13 empty] | 0 | 120 | 10 | 90 | 0 | 40 | 0 | 0
LOCATION: CCR
Equipment Type | CKT TYPE | Unit | SDO | SDI | DO | DI | SAO | SAI | AI | AO | QTY |  | SDO | SDI | DO | DI | SAO | SAI | AI | AO
400V Switchgear Incomer (HVAC MCC) | INC_LV | ECS | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0 | 5 |  | 0 | 60 | 10 | 30 | 0 | 45 | 0 | 0
Distribution Boards and Sub-Distribution Boards | DB | ECS | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 7 |  | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0
AC UPS System | AC_UPS | ECS | 0 | 19 | 0 | 6 | 0 | 5 | 0 | 0 | 4 |  | 0 | 76 | 0 | 24 | 0 | 20 | 0 | 0
ICSS Interface | ICSS | ECS | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |  | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 0
[13 empty] | 4 | 202 | 14 | 91 | 1 | 86 | 0 | 0
[13 empty] | 10 | 210 | 20 | 100 | 10 | 90 | 0 | 0
LOCATION: MAIN SUBSTATION
Equipment Type | CKT TYPE | Unit | SDO | SDI | DO | DI | SAO | SAI | AI | AO | QTY |  | SDO | SDI | DO | DI | SAO | SAI | AI | AO
11kV Switchgear Incomer | INC_11kV | ECS | 0 | 15 | 2 | 7 | 0 | 7 | 2 | 0 | 2 |  | 0 | 30 | 4 | 14 | 0 | 14 | 4 | 0
11kV Bus Tie Breaker | TIE_11kV | ECS | 0 | 18 | 2 | 9 | 0 | 9 | 0 | 0 | 1 |  | 0 | 18 | 2 | 9 | 0 | 9 | 0 | 0
11kV Emergency Diesel Generator Incomer Feeder | GEN_TIE | ECS | 0 | 12 | 2 | 4 | 7 | 0 | 0 | 0 | 1 |  | 0 | 12 | 2 | 4 | 7 | 0 | 0 | 0
11kV Emergency Diesel Generator Package | EDG | ECS | 0 | 23 | 9 | 18 | 0 | 0 | 0 | 0 | 1 |  | 0 | 23 | 9 | 18 | 0 | 0 | 0 | 0
11kV Switchgear Outgoing Transformer Feeder | TR | ECS | 0 | 21 | 3 | 2 | 0 | 9 | 6 | 0 | 9 |  | 0 | 189 | 27 | 18 | 0 | 81 | 54 | 0
11kV Switchgear Outgoing Power Feeder | FDR_11kV | ECS | 0 | 15 | 2 | 2 | 0 | 9 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11kV Switchgear VSD Outgoing Power Feeder | VSD_11kV | ECS | 0 | 14 | 3 | 4 | 0 | 9 | 0 | 0 | 2 |  | 0 | 28 | 6 | 8 | 0 | 18 | 0 | 0
11kV DOL Starter Motor Feeder | DOL_11kV | ECS | 0 | 23 | 3 | 3 | 0 | 9 | 0 | 0 | 4 |  | 0 | 92 | 12 | 12 | 0 | 36 | 0 | 0
690V Switchgear Incomer | INC_LV | ECS | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0 | 10 |  | 0 | 120 | 20 | 60 | 0 | 90 | 0 | 0
400V Switchgear Incomer | INC_LV | ECS | 0 | 12 | 2 | 6 | 0 | 9 | 0 | 0 | 4 |  | 0 | 48 | 8 | 24 | 0 | 36 | 0 | 0
690V Bus Tie Breaker | TIE_LV | ECS | 0 | 14 | 2 | 11 | 0 | 9 | 0 | 0 | 3 |  | 0 | 42 | 6 | 33 | 0 | 27 | 0 | 0
400V Bus Tie Breaker | TIE_LV | ECS | 0 | 14 | 2 | 11 | 0 | 9 | 0 | 0 | 1 |  | 0 | 14 | 2 | 11 | 0 | 9 | 0 | 0
690V Switchgear Emergency Switchgear Incomer Feeder | INC_LV_EM | ECS | 0 | 13 | 2 | 7 | 0 | 6 | 0 | 0 | 1 |  | 0 | 13 | 2 | 7 | 0 | 6 | 0 | 0
690V Heater Panel Feeder | H1_LV | ECS | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0
690V Heater and Thyristor Control Panel Feeder | H2_LV | ECS | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 18 |  | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0
690V DOL Starter (Types D1 & E1) | DOL_LV | ECS | 0 | 10 | 0 | 2 | 0 | 0 | 0 | 0 | 7 |  | 0 | 70 | 0 | 14 | 0 | 0 | 0 | 0
690V / 400V Switchgear Panel with VSD | VSD_LV | ECS | 0 | 10 | 0 | 3 | 0 | 0 | 0 | 0 | 4 |  | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0
690V / 400V Soft Starter | VSD_LV | ECS | 0 | 10 | 0 | 3 | 0 | 0 | 0 | 0 | 4 |  | 0 | 40 | 0 | 12 | 0 | 0 | 0 | 0
400V DOL Starter (Type C1) | DOL_C1_LV | ECS | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC UPS System | AC_UPS | ECS | 0 | 19 | 0 | 6 | 0 | 5 | 0 | 0 | 2 |  | 0 | 38 | 0 | 12 | 0 | 10 | 0 | 0
DC UPS System | DC_UPS | ECS | 0 | 12 | 0 | 5 | 0 | 4 | 0 | 0 | 1 |  | 0 | 12 | 0 | 5 | 0 | 4 | 0 | 0
Distribution Boards and Sub-Distribution Boards | DB | ECS | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4 |  | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0
[13 empty] | 0 | 937 | 104 | 307 | 10 | 350 | 76 | 0
[13 empty] | 0 | 950 | 110 | 320 | 10 | 350 | 100 | 0
ECS LOCATIONS | SDO | SDI | DO | DI | SAO | SAI | AI | AO
LOCATION: ITR PROCESS | 0 | 120 | 10 | 90 | 0 | 40 | 0 | 0 |  |  |  |  | 0 | 120 | 10 | 90 | 0 | 40 | 0 | 0
LOCATION: ITR UTILITY | 0 | 120 | 10 | 90 | 0 | 40 | 0 | 0 |  |  |  |  | 0 | 120 | 10 | 90 | 0 | 40 | 0 | 0
LOCATION: CCR | 10 | 210 | 20 | 100 | 10 | 90 | 0 | 0 |  |  |  |  | 10 | 210 | 20 | 100 | 10 | 90 | 0 | 0
LOCATION: MAIN SUBSTATION | 0 | 950 | 110 | 320 | 10 | 350 | 100 | 0 |  |  |  |  | 0 | 950 | 110 | 320 | 10 | 350 | 100 | 0
Note on L11: HEC: added HVAC MCC

## 70-IJ-61-0001
SWGR/MCC No. | Bus | Equipment Tag No. | Description | Service | Load Type | kV | Starter | Duty | 세로 막대형1 | Abs. kW \[A] | Rated kW \[B] | FLC (A) | PF | UF % | E kW / kVAr | F kW / kVAr | S kW / kVAr | Breaker
70-IJ-61-0001 | A | 70‑KA‑31‑1003 | Export Compressor – Main Motor | N | VSD‑HV | 11 | VVVF | C |  | 10237 | 11000 | 613.615 | 0.97 | 100 | 10553.61 / 2644.98 | – | – | 1250 | VCB
70-IJ-61-0001 | B | 70‑KA‑31‑2003 | Export Compressor – Main Motor | N | VSD‑HV | 11 | VVVF | C |  | 10237 | 11000 | 613.615 | 0.97 | 100 | 10553.61 / 2644.98 | – | – | 1250 | VCB
70-IJ-61-0001 | A | 70‑A‑20‑0002A (Main) | Condensate Recycle Booster Pump A | N | M‑HV | 11 | DOL | I |  | 539 | 720 | 46.799 | 0.85 | 30 | – | 170.21 / 105.49 | – | 630 | VCB
70-IJ-61-0001 | B | 70‑A‑20‑0002B (Main) | Condensate Recycle Booster Pump B | N | M‑HV | 11 | DOL | S |  | 539 | 720 | 46.799 | 0.85 | 10 | – | – | 56.74 / 35.16 | 630 | VCB
70-IJ-61-0001 | A | 70‑KA‑31‑1001/1002‑Main | Flash Gas Compressor – Main Motor | N | M‑HV | 11 | DOL | C |  | 1044 | 1500 | 97.498 | 0.85 | 100 | 1098.95 / 681.07 | – | – | 630 | VCB
70-IJ-61-0001 | B | 70‑PA‑01‑0002 (Main) | Electric Firewater Pump Motor | N | M‑HV | 11 | DOL | I |  | 311 | 400 | 25.999 | 0.85 | 30 | – | 98.21 / 60.87 | – | 400 | VCB
70-IJ-61-0001 | A | 70‑UZ‑43‑0002 | 11/0.72 kV TR for MEG Reboiler (2×100%) | N | F (TR) | 11 | – | C |  | 3100 | 3100 | 171.271 | 1 | 100 | 3263.16 / 0.00 | – | – | 630 | VCB
70-IJ-61-0001 | B | 70‑UZ‑43‑0002‑SP | 11/0.72 kV TR for MEG Reboiler – Spare | N | F (TR) | 11 | – | S |  | 3100 | 3100 | 171.271 | 1 | 10 | – | – | 326.32 / 0.00 | 630 | VCB
70-IJ-61-0001 | B | 70‑HE‑35‑0001‑TR | 11/0.72 kV TR for Start‑up Gas Heater | N | F (TR) | 11 | – | I |  | 530 | 750 | 41.437 | 1 | 30 | – | 167.37 / 0.00 | – | 630 | VCS
70-IJ-61-0001 | A | 70‑IV‑61‑0001A | 11/0.72 kV TR Feeder A → 690V Normal (A) | N | F (Feeder) | 11 | – | C |  | – | – | — | – | – | 198.14 / 8.66 | – | – | 630 | VCB
70-IJ-61-0001 | B | 70‑IV‑61‑0001B | 11/0.72 kV TR Feeder B → 690V Normal (B) | N | F (Feeder) | 11 | – | C |  | – | – | — | – | – | 322.14 / 44.46 | – | – | 630 | VCB
70-IJ-61-0001 | A | 70‑IV‑61‑0003A | 11/0.72 kV TR Feeder A → 690V Normal (A) | N | F (Feeder) | 11 | – | C |  | – | – | — | – | – | 79.26 / 28.36 | – | – | 630 | VCB
70-IJ-61-0001 | B | 70‑IV‑61‑0003B | 11/0.72 kV TR Feeder B → 690V Normal (B) | N | F (Feeder) | 11 | – | C |  | – | – | — | – | – | 70.98 / 30.08 | – | – | 630 | VCS
70-IJ-61-0001 | A | 70‑IV‑61‑0002A | 11/0.42 kV TR Feeder A → 400V Normal (A) | N | F (Feeder) | 11 | – | C |  | – | – | — | – | – | 49.51 / 32.78 | – | – | 630 | VCB
70-IJ-61-0001 | B | 70‑IV‑61‑0002B | 11/0.42 kV TR Feeder B → 400V Normal (B) | N | F (Feeder) | 11 | – | C |  | – | – | — | – | – | 37.55 / 24.15 | – | – | 630 | VCB
|  |  | Incomer 1 | [14 empty] | 4000 | VCB
|  |  | Incomer 2 | [8 empty] | 4000 | [5 empty] | 4000 | VCB
|  |  | Bus Tie | [8 empty] | 4000 | [5 empty] | 4000 | VCB
|  |  | Equipped Spare 1 | [8 empty] | 630 | [5 empty] | 630 | VCB
|  |  | Equipped Spare 1 | [8 empty] | 1250 | [5 empty] | 1250 | VCB
|  |  | Equipped Spare 2 | [8 empty] | 630 | [5 empty] | 400 | VCS
|  | 24.56 | [12 empty] | 362
50.79
Calculation for 4000A Breaker by Interpolation
Given as per table:
[13 empty] | Q4k | (4000/3000)^2 x 2500
[13 empty] | Q4k | 4444.4444
tr
[13 empty] | Q630 | (630/1200)^2 x 250
[13 empty] | Q630 | 68.9062
0.20074
| Bus | Equipment Tag No. | Description | Service | Load Type | kV | Starter | Duty | Abs. kW [A] | Rated kW [B] | Eff % | PF | UF % | E kW / kVAr | F kW / kVAr | S kW / kVAr
| A | 70‑KA‑31‑1003 | Export Compressor – Main Motor | N | VSD‑HV | 11 | VVVF | C | 10237 | 11000 | 97 | 0.97 | 100 | 10553.61 / 2644.98 | – | –
| B | 70‑KA‑31‑2003 | Export Compressor – Main Motor | N | VSD‑HV | 11 | VVVF | C | 10237 | 11000 | 97 | 0.97 | 100 | 10553.61 / 2644.98 | – | –
| A | 70‑A‑20‑0002A (Main) | Condensate Recycle Booster Pump A | N | M‑HV | 11 | DOL | I | 539 | 720 | 95 | 0.85 | 30 | – | 170.21 / 105.49 | –
| B | 70‑A‑20‑0002B (Main) | Condensate Recycle Booster Pump B | N | M‑HV | 11 | DOL | S | 539 | 720 | 95 | 0.85 | 10 | – | – | 56.74 / 35.16
| A | 70‑KA‑31‑1001/1002‑Main | Flash Gas Compressor – Main Motor | N | M‑HV | 11 | DOL | C | 1044 | 1500 | 95 | 0.85 | 100 | 1098.95 / 681.07 | – | –
| B | 70‑PA‑01‑0002 (Main) | Electric Firewater Pump Motor | N | M‑HV | 11 | DOL | I | 311 | 400 | 95 | 0.85 | 30 | – | 98.21 / 60.87 | –
| A | 70‑UZ‑43‑0002 | 11/0.72 kV TR for MEG Reboiler (2×100%) | N | F (TR) | 11 | – | C | 3100 | 3100 | 95 | 1 | 100 | 3263.16 / 0.00 | – | –
| B | 70‑UZ‑43‑0002‑SP | 11/0.72 kV TR for MEG Reboiler – Spare | N | F (TR) | 11 | – | S | 3100 | 3100 | 95 | 1 | 10 | – | – | 326.32 / 0.00
| B | 70‑HE‑35‑0001‑TR | 11/0.72 kV TR for Start‑up Gas Heater | N | F (TR) | 11 | – | I | 530 | 750 | 95 | 1 | 30 | – | 167.37 / 0.00 | –
| A | 70‑IV‑61‑0001A | 11/0.72 kV TR Feeder A → 690V Normal (A) | N | F (Feeder) | 11 | – | C | – | – | – | – | – | 198.14 / 8.66 | – | –
| B | 70‑IV‑61‑0001B | 11/0.72 kV TR Feeder B → 690V Normal (B) | N | F (Feeder) | 11 | – | C | – | – | – | – | – | 322.14 / 44.46 | – | –
| A | 70‑IV‑61‑0003A | 11/0.72 kV TR Feeder A → 690V Normal (A) | N | F (Feeder) | 11 | – | C | – | – | – | – | – | 79.26 / 28.36 | – | –
| B | 70‑IV‑61‑0003B | 11/0.72 kV TR Feeder B → 690V Normal (B) | N | F (Feeder) | 11 | – | C | – | – | – | – | – | 70.98 / 30.08 | – | –
| A | 70‑IV‑61‑0002A | 11/0.42 kV TR Feeder A → 400V Normal (A) | N | F (Feeder) | 11 | – | C | – | – | – | – | – | 49.51 / 32.78 | – | –
| B | 70‑IV‑61‑0002B | 11/0.42 kV TR Feeder B → 400V Normal (B) | N | F (Feeder) | 11 | – | C | – | – | – | – | – | 37.55 / 24.15 | – | –

## 70-IK-61-0001
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | BREAKER | Heat Dissipation
70-DM-01-0004A | C | 90 | 76.7832 | M-B1 | 400V DOL Motor Starter Cubicle | 16E | [8 empty] | 20% SPARE | REMARKS
70-DM-01-0004B | C | 90 | 76.7832 | M-B1 | 400V DOL Motor Starter Cubicle | 16E | [5 empty] | BUS A | M-B1 | 9 | 3 | 36E
70-HF-05-0001A | C | 65 | 13.2894 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | F | 16 | 5 | 8E
70-HF-05-0001B | C | 65 | 13.2894 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [6 empty] | U | 29 | 9 | 8E
70-GU-06-0001A | A | 5 | 4.922 | U | 400V UPS Feeder Cubicle | 8E/4 | [6 empty] | M-E1 | 0 | 0 | 36E
70-GU-06-0001B | C | 5 | 4.922 | U | 400V UPS Feeder Cubicle | 8E/4 | [6 empty] | H | 5 | 2
70-GU-06-0002A | A | 10 | 6.3198 | U | 400V UPS Feeder Cubicle | 8E/4 | [6 empty] | M-A1 | 9 | 3
70-GU-06-0002B | C | 10 | 6.3198 | U | 400V UPS Feeder Cubicle | 8E/4 | [6 empty] | L | 11 | 4
70-GU-06-0002 | B | 10 | 6.3198 | U | 400V UPS Feeder Cubicle | 8E/4
70-GU-06-0003A | A | 25 | 18.1425 | U | 400V UPS Feeder Cubicle | 8E/4
70-GU-06-0003B | C | 25 | 18.1425 | U | 400V UPS Feeder Cubicle | 8E/4 | [5 empty] | BUS B | M-B1 | 9 | 2 | 36E
70-GU-06-0003 | B | 25 | 18.1425 | U | 400V UPS Feeder Cubicle | 8E/4 | [6 empty] | F | 16 | 4 | 8E
70-GU-06-0004A | A | 100 | 78.5452 | U | 400V UPS Feeder Cubicle | 8E | [6 empty] | U | 29 | 6 | 8E
70-GU-06-0004B | C | 100 | 78.5452 | U | 400V UPS Feeder Cubicle | 8E | [6 empty] | M-E1 | 0 | 0 | 36E
70-GU-06-0004 | B | 100 | 78.5452 | U | 400V UPS Feeder Cubicle | 8E | [6 empty] | H | 5 | 1
70-GU-06-0005A | A | 15 | 9.4502 | U | 400V UPS Feeder Cubicle | 8E/4 | [6 empty] | M-A1 | 9 | 2
70-GU-06-0005B | C | 15 | 9.4502 | U | 400V UPS Feeder Cubicle | 8E/4 | [6 empty] | L | 11 | 3
70-GU-06-0005 | B | 15 | 9.4502 | U | 400V UPS Feeder Cubicle | 8E/4
70-GU-06-0006A | A | 80 | 62.7259 | U | 400V UPS Feeder Cubicle | 8E
70-GU-06-0006B | C | 80 | 62.7259 | U | 400V UPS Feeder Cubicle | 8E | [7 empty] | 158 | 44
70-GU-06-0006 | B | 80 | 62.7259 | U | 400V UPS Feeder Cubicle | 8E
70-GU-06-0007A | A | 100 | 70.2566 | U | 400V UPS Feeder Cubicle | 8E
70-GU-06-0007B | C | 100 | 70.2566 | U | 400V UPS Feeder Cubicle | 8E
70-GU-06-0007 | B | 100 | 70.2566 | U | 400V UPS Feeder Cubicle | 8E | [8 empty] | feeder qty | 30% SPARE
70-GU-06-0008A | A | 100 | 97.5245 | U | 400V UPS Feeder Cubicle | 8E | [5 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 16E | 2 | 1 | 3 | 400V DOL Motor Starter Cubicle (M-B1): 3 EACH
70-GU-06-0008B | C | 100 | 97.5245 | U | 400V UPS Feeder Cubicle | 8E | [5 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | 4 | 2 | 6 | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4): 6 EACH
70-GU-06-0008 | B | 100 | 97.5245 | U | 400V UPS Feeder Cubicle | 8E | [5 empty] | U | 400V UPS Feeder Cubicle | 8E/4 | 14 | 5 | 19 | 400V UPS Feeder Cubicle: 19 EACH
70-GU-06-0010A | A | 20 | 11.7833 | U | 400V UPS Feeder Cubicle | 8E/4 | [5 empty] | U | 400V UPS Feeder Cubicle | 8E | 15 | 5 | 20 | 400V UPS Feeder Cubicle: 20 EACH
70-GU-06-0010B | C | 20 | 11.7833 | U | 400V UPS Feeder Cubicle | 8E/4 | [5 empty] | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | 8 | 1 | 9 | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) (F): 9 EACH
70-GU-06-0010 | B | 20 | 11.7833 | U | 400V UPS Feeder Cubicle | 8E/4 | [5 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 5 | 2 | 7 | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8): 7 EACH
70-GU-06-0011A | A | 60 | 41.3251 | U | 400V UPS Feeder Cubicle | 8E | [5 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4 | 10 | 3 | 13 | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5): 13 EACH
70-GU-06-0011B | C | 60 | 41.3251 | U | 400V UPS Feeder Cubicle | 8E | [5 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 1 | 1 | 2 | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4): 2 EACH
70-GU-06-0011 | B | 60 | 41.3251 | U | 400V UPS Feeder Cubicle | 8E | [5 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 72E | 1 | 0 | 1 | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5): 1 EACH
70-IV-09-0003A | C | 630 | 1000 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [5 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E | 3 | 1 | 4 | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) (F): 4 EACH
70-IV-09-0003B | A | 630 | 1000 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [5 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 8E | 7 | 3 | 10 | 400V DOL Motor Starter Cubicle (M-B1): 10 EACH
70-IV-09-0005A | C | 400 | 630 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [5 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | 8 | 3 | 11 | 400V DOL Motor Starter Cubicle: 11 EACH
70-IV-09-0005B | A | 400 | 630 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [5 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 8E | 1 | 1 | 2
70-IV-09-0006A | C | 400 | 630 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E
70-IV-09-0006B | A | 400 | 630 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [5 empty] | Total Heat Dissipation
70-IV-09-0007A | C | 400 | 630 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [5 empty] | 6750
70-IV-09-0007B | A | 400 | 630 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E
70-HE-36-0002A | A | 450 | 227.5931 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-HE-36-0002B | C | 450 | 227.5931 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-HE-36-0003 | C | 320 | 222.5727 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-IV-62-0001 | C | 5 | 3.4946 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0002 | C | 5 | 3.4946 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0003 | C | 15 | 12.7972 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0006 | C | 15 | 11.2222 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0007 | C | 30 | 23.6256 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0009 | C | 15 | 14.766 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0011 | C | 15 | 13.88 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0013 | C | 32 | 26.5788 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0014 | C | 32 | 26.5788 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0015 | C | 32 | 26.5788 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0051 | C | 32 | 22.149 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-IV-62-0052 | C | 32 | 19.1958 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-IV-65-0080 | C | 85 | 50.2044 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E
70-IV-62-0094 | C | 400 | 630 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 72E
70-UA-07-0001A-Main Motor | C | 400 | 374.0718 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E
70-UA-07-0001B-Main Motor | A | 400 | 374.0718 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E
70-UA-07-0001C-Main Motor | B | 400 | 374.0718 | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E
70-UA-07-0001A-Cooling Fan Motor 1 (100% x 2) | C | 30 | 27.5512 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-UA-07-0001A-Cooling Fan Motor 2 (100% x 2) | C | 30 | 27.5512 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-UA-07-0001A-Container Fan Motor 1 (100% x 2) | C | 3 | 2.7551 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UA-07-0001A-Container Fan Motor 2 (100% x 2) | C | 3 | 2.7551 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UA-07-0001B-Cooling Fan Motor 1 (100% x 2) | A | 30 | 27.5512 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-UA-07-0001B-Cooling Fan Motor 2 (100% x 2) | B | 30 | 27.5512 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-UA-07-0001B-Container Fan Motor 1 (100% x 2) | A | 3 | 2.7551 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UA-07-0001B-Container Fan Motor 2 (100% x 2) | B | 3 | 2.7551 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UA-07-0001C-Cooling Fan Motor 1 (100% x 2) | A | 30 | 27.5512 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-UA-07-0001C-Cooling Fan Motor 2 (100% x 2) | B | 30 | 27.5512 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-UA-07-0001C-Container Fan Motor 1 (100% x 2) | A | 3 | 2.7551 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UA-07-0001C-Container Fan Motor 2 (100% x 2) | B | 3 | 2.7551 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-36-0001A Motor | C | 18.5 | 15.0001 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-PA-36-0001B Motor | C | 18.5 | 15.0001 | M-A1 | 400V DOL Motor Starter Cubicle | 8E
70-PA-36-0004A Motor | C | 11 | 5.648 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-36-0004B Motor | B | 11 | 5.648 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-HE-36-0005A | A | 450 | 227.5931 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-HE-36-0005B | C | 450 | 227.5931 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-HE-36-0005B | [7 empty] | CANCELLED
70-UA-07-0001C-Cooling Fan Motor 1 (100% x 2) | [7 empty] | CANCELLED
70-UA-07-0001C-Cooling Fan Motor 2 (100% x 2) | [7 empty] | CANCELLED
70-UA-07-0001C-Container Fan Motor 1 (100% x 2) | [7 empty] | CANCELLED
70-UA-07-0001C-Container Fan Motor 2 (100% x 2) | [7 empty] | CANCELLED
70-PA-36-0001A Motor | [7 empty] | CANCELLED
70-PA-36-0001B Motor | [7 empty] | CANCELLED
70-PA-36-0004A Motor | [7 empty] | CANCELLED
70-PA-36-0004B Motor | [7 empty] | CANCELLED
70-HE-36-0005A | [7 empty] | CANCELLED
70-HE-36-0005B | [7 empty] | CANCELLED
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 16E | 1
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | 2
|  |  |  | U | 400V UPS Feeder Cubicle | 8E/4 | 5
|  |  |  | U | 400V UPS Feeder Cubicle | 8E | 5
|  |  |  | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | 1
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 2
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4 | 3
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 1
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 72E | 0
|  |  |  | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E | 1
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 8E | 3
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | 3
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E | 1
[11 empty] | TARGET | 21000
[11 empty] | SAVED SPACE | 2200
[9 empty] | MCC(single) | INC & BUS-TIE&ACB | Dummy |  | NER PANEL
[9 empty] | 18000 | 4000 | 1200 | 23200
[9 empty] | 14 | 5 | 3 | 26 | 3 | 29
[9 empty] | 4 |  |  | SPARE PANEL
arrange=, capE=72, totalE=216
BUS A
[5 empty] | BUS B |  |  |  | A | 6 | 1 | 7 | 1 | 8
[9 empty] | B | 2 | 1 | 3 | 1 | 4
[9 empty] | C | 8 |  | 8 | 1 | 9
[10 empty] | 72E |  |  |  | 29
|  |  |  | M-HV → HV DOL motor starter |  |  |  |  | A | 4 | 1 | 5
|  |  |  | M-A1/B1/C1/D1/E1 → LV DOL motor starter |  |  |  |  | B | 0 |  | 0
|  |  |  | VSD-HV → HV VSD / Soft Starter |  |  |  |  | C | 5 |  | 5
|  |  |  | VSD-G1 / VSD-G2 → LV VSD / Soft Starter | [5 empty] | Full Panel
|  |  |  | F / P → Circuit breaker feeder |  |  |  |  | A | 2 |  | 2
|  |  |  | L → Lighting load |  |  |  |  | B | 2 | 1 | 3
|  |  |  | U → UPS feeder |  |  |  |  | C | 3 |  | 3
H → Heater load
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 16E
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
|  |  |  | U | 400V UPS Feeder Cubicle | 8E/4
|  |  |  | U | 400V UPS Feeder Cubicle | 8E
|  |  |  | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 72E
|  |  |  | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 8E
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E

## 70-IK-61-0002
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | BREAKER | Heat Dissipation
70-KA-31-1003 Main Lube Oil Pump Motor | A | 15 | 22.9242 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1003 S/b Lube Oil Pump Motor | B | 15 | 22.9242 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1003 LO reservoir Heater | A | 30 | 45.8484 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-KA-31-1003 LO Cooler Fan Motor 1 | A | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1003 LO Cooler Fan Motor 2 | B | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1003 LO Cooler Fan Motor 3 | A | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1003 Oil Mist Eliminator Fan Motor | B | 1 | 1.5283 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1003 VFD | A | 15 | 22.9242 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-KA-31-2003 Main Lube Oil Pump Motor | A | 15 | 22.9242 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-2003 S/b Lube Oil Pump Motor | B | 15 | 22.9242 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-2003 LO reservoir Heater | A | 30 | 45.8484 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-KA-31-2003 LO Cooler Fan Motor 1 | A | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-2003 LO Cooler Fan Motor 2 | B | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-2003 LO Cooler Fan Motor 3 | A | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-2003 Oil Mist Eliminator Fan Motor | B | 1 | 1.5283 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-2003 VFD | A | 15 | 22.9242 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-KA-31-1001/1002-Aux Lube Oil Pump Motor | A | 5.5 | 8.4055 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1001/1002-Main CW Pump Motor | B | 7.5 | 11.4621 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1001/1002-Aux CW Pump Motor | A | 7.5 | 11.4621 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1001/1002-LO Heater | A | 3 | 4.5848 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-KA-31-1001/1002-Coolant Heater | B | 30 | 45.8484 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-KA-31-1001/1002-Electric Barring Device Motor | A | 1.5 | 2.2924 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1001/1002-LO Cooler Fan Motor 1 | A | 7.5 | 11.4621 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1001/1002-LO Cooler Fan Motor 2 | B | 7.5 | 11.4621 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [8 empty] | feeder qty | 30% SPARE | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-KA-31-1001/1002-CW Console Cooler Fan Motor 1 | A | 11 | 16.8111 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [8 empty] | 141 | 45 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-KA-31-1001/1002-CW Console Cooler Fan Motor 2 | A | 11 | 16.8111 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [5 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | 70 | 21 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-PA-01-0001A Hydraulic Motor | A | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [5 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 5 | 2 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-PA-01-0001B Hydraulic Motor | B | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [5 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | 40 | 12 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E
70-PA-01-0001C Hydraulic Motor | B | 5 | 7.6414 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [5 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4 | 5 | 2 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-HF-01-0002 | B | 5 | 6.4527 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | [5 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 3 | 1 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-PA-01-0003A(Main Motor Power) | A | 75 | 110.3758 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [5 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4 | 2 | 1 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 12E
70-PA-01-0003B(Main Motor Power) | B | 75 | 110.3758 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [5 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 12 | 4 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 24E
70-PS-28-0001A Motor | A | 3.7 | 2.6403 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [5 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 16E | 2 | 1 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 16E
70-PS-28-0001A Seal Motor | A | 0.55 | 0.70409 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [5 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 8E | 2 | 1 | M-B1 | 400V DOL Motor Starter Cubicle | 12E
70-PS-28-0001B Motor | B | 3.7 | 2.6403 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | [10 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 8E
70-PS-28-0001B Seal Motor | B | 0.55 | 0.70409 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PS-28-0004A Motor | A | 7.5 | 10.8614 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PS-28-0004B Motor | B | 7.5 | 10.8614 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PS-28-0005A Motor | A | 15 | 20.5681 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PS-28-0005B Motor | B | 15 | 20.5681 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-DM-31-1003 | A | 0.75 | 0.057735 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-43-0001A | A | 11 | 15.4019 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-43-0001B | B | 11 | 15.4019 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-43-0002-C | A | 5.5 | 9.9232 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-43-0002-D | B | 5.5 | 9.9232 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-43-0002-E | A | 15 | 26.4032 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-43-0002-F | B | 15 | 26.4032 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-43-0002-G | A | 4 | 7.2169 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-43-0002-H | B | 4 | 7.2169 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-43-0003A | A | 7.5 | 4.5105 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-43-0003B | B | 7.5 | 4.5105 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-43-0004 | B | 7.5 | 6.5493 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-IV-62-0054 | A | 5 | 3.566 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0055 | A | 5 | 3.566 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
70-IV-62-0056A | A | 30 | 44.9994 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0056B | B | 30 | 49.2446 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0059A | A | 30 | 41.6032 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0059B | B | 30 | 44.1503 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0060 | B | 30 | 40.7541 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0061 | A | 50 | 67.9236 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0062A | A | 30 | 39.056 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0062B | B | 30 | 40.7541 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0064A | A | 30 | 47.5465 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0064B | B | 30 | 42.4522 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-66-0002 | A |  | 125 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E
70-IV-62-0093 | B | 170 | 400 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-IV-62-0099 | B | 12.6 | 125 | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
70-UZ-71-0001-A | A | 2.2 | 3.9693 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-71-0001-B | B | 2.2 | 3.9693 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-72-0001A | A | 90 | 134.4887 | M-B1 | 400V DOL Motor Starter Cubicle | 16E
70-PA-72-0001B | B | 90 | 134.4887 | M-B1 | 400V DOL Motor Starter Cubicle | 16E
70-UZ-72--0001A (70-HF-72-0001A) | A | 11 | 16.9809 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-UZ-72--0001B (70-HF-72-0001B) | B | 11 | 16.9809 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-UB-74-0001 Elec Heater A | B | 25 | 33.9618 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-UB-74-0001 Elec. Heater B | B | 25 | 33.9618 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-UI-75-0001-Pump A | A | 1.5 | 2.4283 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UI-75-0001-Pump B | A | 1.5 | 2.4283 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UI-75-0001-Agitator | A | 4 | 6.4527 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UI-75-0001-Filling Pump | A | 2.2 | 3.549 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UI-75-0002-Pump A | B | 0.25 | 0.40754 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UI-75-0002-Pump B | B | 0.25 | 0.40754 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UI-75-0002-Agitator | B | 0.37 | 0.59433 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UI-75-0002-Filling Pump | B | 0.75 | 1.2056 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-75-0001-Pump A | B | 22 | 35.4901 | M-A1 | 400V DOL Motor Starter Cubicle | 8E
70-UZ-75-0001-Pump B | B | 22 | 35.4901 | M-A1 | 400V DOL Motor Starter Cubicle | 8E
70-DM-85-0001A | A | 11 | 10.2092 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-DM-85-0001B | B | 11 | 10.2092 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-28-0007A | A | 15 | 19.8904 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-PA-28-0007B | B | 15 | 19.8904 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-36-0003-Liquid Ring Recirculation Pump | A | 15 | 23.7629 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-36-0003-Liquid Ring Air Cooler | B | 15 | 23.7629 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-36-0003-LO Heater for 70-KG-36-0003A | A | 3 | 4.7526 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-UZ-36-0003-LO Heater for 70-KG-36-0003B | B | 3 | 4.7526 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-UZ-36-0006-Liquid Ring Recirculation Pump | A | 15 | 23.7629 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-36-0006-Liquid Ring Air Cooler | B | 15 | 23.7629 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-36-0006-LO Heater for 70-KG-36-0006A | A | 3 | 4.7526 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-UZ-36-0006-LO Heater for 70-KG-36-0006B | B | 3 | 4.7526 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-UU-85-0001_Sub item_3 | A | 1 | 1.4082 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-UU-28-0001_Sub Item 2.1.1 | A | 0.75 | 1.0561 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 2.1.2 | B | 0.75 | 1.0561 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 2.1.3 | A | 0.75 | 1.0561 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 2.1.4 | B | 0.75 | 1.0561 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 2.1.5 | A | 0.75 | 1.0561 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 2.2 | B | 2.2 | 3.098 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 3.1 | A | 0.4 | 0.56327 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 3.2 | B | 0.4 | 0.56327 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UU-28-0001_Sub Item 4 | A | 0.75 | 1.0561 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-JC-78-0002 | B | 10 | 15.8419 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-JC-78-0003 | A | 10 | 15.8419 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-JH-78-0001 | A | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-JH-78-0002 | B | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-JH-78-0003 | A | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-JH-78-0004 | B | 5 | 7.921 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
EV-0001 (Temp) | B | 18 | 26.7553 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-CEMS-72-0001A (HOLD) | A | 1.79 | 5.4796 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-CEMS-72-0001B (HOLD) | B | 1.79 | 5.4796 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-UN-26-0001 | A | 2.4 | 7.35 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-UN-35-0002 | B | 2.4 | 7.35 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-UN-35-0003 | A | 2.4 | 7.35 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-UN-35-0004 | B | 2.4 | 7.35 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
82-TRU-87-0001 | A | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
83-TRU-87-0001 | B | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
84-TRU-87-0001 | A | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
86-TRU-87-0001 | B | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
87-TRU-87-0001 | A | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1001 | B | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1002 | A | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1011 | B | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1012 | A | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1013 | B | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1014 | A | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1003 | B | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1004 | A | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1005 | B | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1006 | A | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1007 | B | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1008 | A | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1009 | B | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1010 | A | 3 | 4.8113 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1015 | B | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-TRU-87-1016 | A | 2 | 3.2075 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
70-PA-36-0001B Motor
70-PA-36-0004A Motor
70-PA-36-0004B Motor
70-UA-07-0001B-Main Motor
70-UA-07-0001C-Main Motor
70-A-20-0002A -Main Oil Pump
70-A-20-0002B -Main Oil Pump
70-A-20-0002A -Aux Oil Pump
70-A-20-0002B -Aux Oil Pump
70-A-20-0002A -Lube Oil Heater
70-A-20-0002B -Lube Oil Heater
70-UA-07-0001A-Cooling Fan Motor 1 (50% x 3)
70-UA-07-0001A-Cooling Fan Motor 2 (50% x 3)
70-UA-07-0001A-Cooling Fan Motor 3 (50% x 3)
70-UA-07-0001A-Container Fan Motor 1 (100% x 2)
70-UA-07-0001A-Container Fan Motor 2 (100% x 2)
70-UA-07-0001B-Cooling Fan Motor 1 (50% x 3)
70-UA-07-0001B-Cooling Fan Motor 2 (50% x 3)
70-UA-07-0001B-Cooling Fan Motor 3 (50% x 3)
70-UA-07-0001B-Container Fan Motor 1 (100% x 2)
70-UA-07-0001B-Container Fan Motor 2 (100% x 2)
70-UA-07-0001C-Cooling Fan Motor 1 (50% x 3)
70-UA-07-0001C-Cooling Fan Motor 2 (50% x 3)
70-UA-07-0001C-Cooling Fan Motor 3 (50% x 3)
70-UA-07-0001C-Container Fan Motor 1 (100% x 2)
70-UA-07-0001C-Container Fan Motor 2 (100% x 2)
70-UZ-36-0006-Liquid Ring Recirculation Pump
70-UZ-36-0006-Liquid Ring Air Cooler
70-UZ-36-0006-LO Heater for 70-KG-36-0006A
70-UZ-36-0006-LO Heater for 70-KG-36-0006B
70-UU-85-0001_Sub item_3
70-JC-78-0001
70-JC-78-0002
70-JC-78-0003
70-JD-78-0008
70-JH-78-0001
70-JH-78-0002
70-JH-78-0003
70-JH-78-0004
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | 21
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 2
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4 | 12
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4 | 2
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 1
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4 | 1
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 4
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 16E | 1
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E | 1
400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1)
16600
2500
[9 empty] | MCC(SINGLE FRONT) | INC & BUS-TIE&ACB | Dummy |  | NER PANEL
[9 empty] | 10000 | 3000 | 1100 | 14100
[9 empty] | 7 | 3 | 2 | 15
3
arrange=, capE=72, totalE=0
[9 empty] | A | 3 | 2 | 5 | 1 | 6
[9 empty] | B | 3 | 2 | 5 | 1 | 6
72E
[9 empty] | A | 0
[9 empty] | B | 0
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E/4
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E/4
|  |  |  | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 16E
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E
Note on D66: HEC: this is assumed
Note on D67: HEC: this is assumed
Note on D68: HEC: this is assumed
Note on H194: HEC: with PFC panel feeder +2

## 70-IK-61-0003
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 30% SPARE
70-HE-28-0001 | B | 84 | 56.8983 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 3 | 1
70-HE-35-0001 | B | 636 | 443.4719 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) |  | RELOCATE TO 11kV | [5 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
70-IV-09-0002A | A | 630 | 1000 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [6 empty] | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | 2 | 1
70-IV-09-0004A | B | 400 | 630 | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 2 | 1
70-IV-09-0010A | A | 63 | 125 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | VSD-G2 | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | 24E | 4 | 2
70-IV-09-0011A | B | 25 | 125 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 16E | 4 | 2
70-DM-36-0003A | A | 355 | 315.0078 | VSD-G2 | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | 24E | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4 | 2 | 1
70-DM-36-0006A | B | 355 | 315.0078 | VSD-G2 | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | 24E | [6 empty] | M-D1 | 400V DOL Motor Starter Cubicle | 16E | 3 | 1
70-PA-25-0001A Motor | A | 250 | 217.5523 | M-E1 | 400V DOL Motor Starter Cubicle | 16E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 8E | 15 | 5
70-PA-25-0001B Motor | B | 250 | 217.5523 | M-E1 | 400V DOL Motor Starter Cubicle | 16E | [6 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | 8 | 3
70-HE-70-0001 A | A | 184 | 128.1048 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-HE-70-0001 B | B | 184 | 128.1048 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
70-PA-20-0001A Motor | A | 250 | 215.5835 | M-E1 | 400V DOL Motor Starter Cubicle | 16E
70-PA-20-0001B Motor | B | 250 | 215.5835 | M-E1 | 400V DOL Motor Starter Cubicle | 16E
70-HE-31-1001 | A | 15 | 10.0409 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-HE-31-1002 | A | 35 | 23.4287 | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
70-DM-43-0001A | A | 185 | 163.9025 | M-D1 | 400V DOL Motor Starter Cubicle | 16E
70-DM-43-0001B | B | 185 | 163.9025 | M-D1 | 400V DOL Motor Starter Cubicle | 16E
70-DM-43-0001C | B | 185 | 163.9025 | M-D1 | 400V DOL Motor Starter Cubicle | 16E
70-DM-36-0003B | B | 355 | 315.0078 | VSD-G2 | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | 24E
70-DM-36-0006B | A | 355 | 315.0078 | VSD-G2 | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | 24E
70-EA-31-1004-A | A | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-1004-B | A | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-1004-C | A | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-1004-D | A | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-1004-E | A | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-1004-F | A | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-2004-A | B | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-2004-B | B | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-2004-C | B | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-2004-D | B | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-2004-E | B | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-2004-F | B | 22 | 19.2246 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-31-1001-A | B | 5.5 | 4.6021 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-EA-31-1001-B | B | 5.5 | 4.6021 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-EA-31-1001-C | A | 5.5 | 4.6021 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-EA-31-1002-A | B | 5.5 | 4.6021 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-EA-31-1002-B | B | 5.5 | 4.6021 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-EA-31-1002-C | A | 5.5 | 4.6021 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-EA-72-0001-A | B | 22 | 17.9593 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-72-0001-B | B | 22 | 17.9593 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-EA-72-0001-C | A | 22 | 17.9593 | M-B1 | 400V DOL Motor Starter Cubicle | 8E
70-UZ-43-0002-A | A | 10 | 9.844 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
70-UZ-43-0002-B | B | 10 | 9.844 | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 1
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 1
|  |  |  | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E | 1
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 1
|  |  |  | VSD-G2 | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | 24E | 2
|  |  |  | M-E1 | 400V DOL Motor Starter Cubicle | 16E | 2
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4 | 1
|  |  |  | M-D1 | 400V DOL Motor Starter Cubicle | 16E | 1
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 8E | 5
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4 | 3
PFC PANEL
6600
[10 empty] | -9.75 | -7800
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 12000 | 2400 | 0 | 14400
[8 empty] | 8 | 3 |  | 18
[8 empty] | 4 |  |  | SPARE PANEL | NER PANEL
[7 empty] | A | 4 |  |  | 2 | 1 | 7
[7 empty] | B | 4 |  |  | 2 | 1 | 7
72E
[7 empty] | A | 1 |  |  | 1
[7 empty] | B | 1
Full Panel
[7 empty] | A | 3 |  |  | 1
[7 empty] | B | 3 |  |  | 2
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E
|  |  |  | F | 400V Air Circuit Breaker(ACB) Feeder Cubicle (per Dwg LV1) | 72E
|  |  |  | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E
|  |  |  | VSD-G2 | 400V MCCB Feeder for VSD Cubicle (per Dwg LV9) | 24E
|  |  |  | M-E1 | 400V DOL Motor Starter Cubicle | 16E
|  |  |  | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E/4
|  |  |  | M-D1 | 400V DOL Motor Starter Cubicle | 16E
|  |  |  | M-B1 | 400V DOL Motor Starter Cubicle | 8E
|  |  |  | M-A1 | 400V DOL Motor Starter Cubicle | 8E/4

## 81-1K-61-0001
TAGS | BUS | RATED POWER | FULL LOAD CURRENT | Starter Type | CIRCUIT TYPE | E_UNITS | REMARKS | [8 empty] | feeder qty | 20% SPARE
81-1K-61-0001 | B | 88.681 | 160 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
81-IG-62-0001 | B | 44.3405 | 80 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | 5 | 1
81-IK-09-0001A | A | 55.4256 | 100 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | [6 empty] | U | 400V UPS Feeder Cubicle | 8E | 0 | 0
81-IK-09-0001B | B | 55.4256 | 100 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | [6 empty] | U | 400V UPS Feeder Cubicle | 12E | 0 | 0
81-GU-06-0001A | A | 22.1703 | 40 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 36E | 0 | 0
81-GU-06-0001B | B | 22.1703 | 40 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 16E | 0 | 0
81-GU-06-0002A | A | 22.1703 | 40 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 16E | 1 | 1
81-GU-06-0002B | B | 22.1703 | 40 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | 4 | 1
SPARE | A | 55.4256 | 100 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 12E | [6 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 16E | 0 | 0
SPARE | B | 22.1703 | 40 | F | 400V MCCB Feeder Cubicle (I < 160A, per Dwg LV4) | 8E | [6 empty] | M-B1 | 400V DOL Motor Starter Cubicle | 24E | 0 | 0
[13 empty] | M-A1 | 400V DOL Motor Starter Cubicle | 16E | 0 | 0
[13 empty] | L | 400V 3Ph+N+PE Feeder Cubicle (per Dwg LV5) | 8E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 12E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 36E | 0 | 0
[13 empty] | F | 400V MCCB Feeder Cubicle (I > 160A, per Dwg LV3) | 8E | 0 | 0
[13 empty] | M-E1 | 400V DOL Motor Starter Cubicle | 8E | 0 | 0
[13 empty] | H | 400V SCR-Controlled Heater Feeder Cubicle (per Dwg LV8) | 8E | 0 | 0
[8 empty] | MCC(SINGLE) | INC & BUS-TIE&ACB | Dummy | TOTAL LENGTH
[8 empty] | 1600 | 1000 | 0 | 2600
[8 empty] | 2 | 1 | 0 | 3
SPARE PANEL

## BOQ
2 | 11kV Switchgear (MR: XXX-MR-EL-001) |  | 0
0
2.1 | 11kV Switchgear |  | 0
| Metal-clad, AIS, Single Busbar, Single Tier, Single Front, VCB(Withdrawable - LSC2B-PM), 'Equipped with Electrical and Mechanical Interlocks and Surge arrestors, IAC type : AFLR Communication Protocol: Modbus + IEC 61850, Protection Relays : Digital.As per P&M diagrams |  | 0
| Indoor Installation, Free-standing, IP21 / IK08, 25ºC Ambient Temperature. Min. 25 years design life for all components. |  | 0
| Mandatory labelling: All MV/HV equipment in English and Azerbaijani. 'ACCESSORIES: 1 x HV Truck |  | 0
| - 70-IJ-61-0001 (11kV, 3ph, 3wire, 4000A, 50Hz, 40kA for 1sec) | PNL | 24
| 25300(W) x 1455(D) x 2696(H) |  | 0
0
0
2.4 | ECS (ELECTRICAL CONTROL SYSTEM) |  | 0
0
2.4.1 | ECS Control Panel |  | 0
| Free standing, Indoor Installation, IP 21, 25ºC Ambient Temperature, Bottom cable entry SM/MM Fiber Optic Patch Box, Ethernet Switch, Hardwire IO Module, Redundant Servers, PLCs |  | 0
| Network Attached Storage (NAS), Data Historian for 5-year storage + archiving (PI Server), Redundant power supply modules, 'Cybersecurity hardware/software, NTP signal provided by ICSS |  | 0
| - XXXXXXX (TBA), Main Substation, Dimension: 800(W) x 800(D) x 2200(H) | SET | 2
| - XXXXXXX (TBA), Beach Valve Station, Dimension: 800(W) x 800(D) x 2200(H) | SET | 2
| For Each Equipment: 800(W) x 800(D) x 2200(H) |  | 0
0
2.4.2 | ECS Workstation + Printer |  | 0
| Free standing, Indoor Installation, IP 21, 25ºC Ambient Temperature, Bottom cable entry SM/MM Fiber Optic Patch Box, Ethernet Switch, Hardwire IO Module, Redundant Servers, PLCs |  | 0
| Network Attached Storage (NAS), Data Historian for 5-year storage + archiving (PI Server), Redundant power supply modules, 'Cybersecurity hardware/software, NTP signal provided by ICSS |  | 0
| - XXXXXXX (TBA), Main Substation & CCR, Dimension: 800(W) x 800(D) x 2200(H) | SET | 2
| - XXXXXXX (TBA), Beach Valve Station, Dimension: 800(W) x 800(D) x 2200(H) | SET | 1
2.4.3 | Portable Maintenance PCs (17” Maintenance Laptop) c/w necessary software for diagnostics and configuration | SET | 2
3 | LV Switchgear (MR: XXX-MR-EL-001) |  | 0
0
3.1 | 690V and 400V Switchgear/MCC |  | 0
| Metal Enclosed, AIS, Single Busbar, ACB(Single Tier), LV MCC(Single Tier), Single Front, Form 4B, Withdrawable, Indoor Installation, Free-standing, IIP21 / IK08, 25ºC Ambient Temperature. |  | 0
| Arcing Class B, Withdrawable - LSC2B-PM, Electrical and Mechanical Interlocks, Communication Protocol: Modbus + IEC 61850, Protection: As per P&M diagrams |  | 0
0
| - 70-IK-61-0001 (690V, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | PNL | 27
| 21000(W) x 1000(D) x 2200(H) |  | 0
0
| - 70-IK-61-0003 (690V, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | PNL | 12
| 8600(W) x 1000(D) x 2200(H) |  | 0
0
| - 70-IK-61-0002 (400V, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | PNL | 22
| 16600(W) x 1000(D) x 2500(H) |  | 0
0
| - 81-1K-61-0001 (400V, 3ph, 4wire, 160A OR 630A, 50Hz, 25kA for 1sec) | PNL | 3
| 2400(W) x 1000(D) x 2200(H) |  | 0
0
0
0
3.5 | 400V BUS DUCT |  | 0
| Non-segregated phase busduct(NSPB), air insulated, totally metal enclosed and self-cooled. |  | 0
| IP 55, 40ºC Ambient Temperature |  | 0
| Rain/Sun Canopy for Outdoor Busduct, Wall penetration fitting & busduct support material including outdoor steel frame/structure |  | 0
| Termination flange at transformer & switchgear end |  | 0
0
3.5.1 | Tag No. 70-BDU-61-0001A/B (0.72kV, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | SET | 1
| Straight: 26meter, Horizontal Bend: 2EA, Vertical Bend: 4EA |  | 0
| Dimension: 485(W) x 555(D) |  | 0
0
0
0
3.5.2 | 70-BDU-61-0001B (0.72kV, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | SET | 1
| Straight: 35 meter, Horizontal Bend: 2 EA, Vertical Bend: 4 EA |  | 0
| Dimension: 485(W) x 555(D) |  | 0
0
0
0
3.5.3 | 70-BDU-61-0001C (0.72kV, 3ph, 4wire, 2500A, 50Hz, 80kA for 1sec) | SET | 1
| Straight: 15 meter, Horizontal Bend: 2 EA, Vertical Bend: 4 EA |  | 0
| Dimension: 485(W) x 555(D) |  | 0
0
0
0
3.5.4 | 70-BDU-61-0003A (0.72kV, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | SET | 1
| Straight: 15 meter, Horizontal Bend: 2 EA, Vertical Bend: 4 EA |  | 0
| Dimension: 485(W) x 555(D) |  | 0
0
0
0
3.5.5 | 70-BDU-61-0003B (0.72kV, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | SET | 1
| Straight: 16 meter, Horizontal Bend: 2 EA, Vertical Bend: 4 EA |  | 0
| Dimension: 485(W) x 555(D) |  | 0
0
0
0
3.5.6 | 70-BDU-61-0002A (400V, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | SET | 1
| Straight: 14 meter, Horizontal Bend: 2 EA, Vertical Bend: 4 EA |  | 0
| Dimension: 485(W) x 555(D) |  | 0
0
0
0
3.5.9 | 70-BDU-61-0002B (400V, 3ph, 4wire, 4000A, 50Hz, 80kA for 1sec) | SET | 1
| Straight: 16 meter, Horizontal Bend: 2 EA, Vertical Bend: 4 EA |  | 0
| Dimension: 485(W) x 555(D) |  | 0
0
0

## Insulation_Mat
✅ Assumptions:
Switchgear footprint:
Width (W) = 25,300 mm = 25.3 m
Depth (D) = 1,455 mm = 1.455 m
Clearance around equipment:
Let’s assume 0.3 m on all sides (typical safety clearance).
✅ Formula for Mat Dimensions:
Mat Width=W+2×Side Clearance\text{Mat Width} = W + 2 \times \text{Side Clearance}Mat Width=W+2×Side Clearance
Mat Depth=D+2×Front/Rear Clearance\text{Mat Depth} = D + 2 \times \text{Front/Rear Clearance}Mat Depth=D+2×Front/Rear Clearance
✅ Calculation:
Mat Width=25.3+(2×0.3)=25.9 m\text{Mat Width} = 25.3 + (2 \times 0.3) = 25.9 \text{ m}Mat Width=25.3+(2×0.3)=25.9 m
Mat Depth=1.455+(2×0.3)=2.055 m\text{Mat Depth} = 1.455 + (2 \times 0.3) = 2.055 \text{ m}Mat Depth=1.455+(2×0.3)=2.055 m
Final Mat Size = 25.9 m × 2.055 m
That’s a continuous mat around the entire switchgear footprint.
If you want full perimeter coverage (like a walkway around), we’d calculate the total perimeter length and mat strip width. For example:
Perimeter=2(W+D)=2(25.3+1.455)=53.51 m\text{Perimeter} = 2(W + D) = 2(25.3 + 1.455) = 53.51 \text{ m}Perimeter=2(W+D)=2(25.3+1.455)=53.51 m
So, you’d need 53.5 m of mat strips (e.g., 1 m wide) to go around.
with 30% spare length
69.55 | meters
Switchgear | Mat Width (m) | Mat Depth (m) | Perimeter (m)
70-IK-61-0001 | 21.6 | 1.6 | 44
70-IK-61-0003 | 9.2 | 1.6 | 19.2
70-IK-61-0002 | 17.2 | 1.6 | 35.2
81-1K-61-0001 | 3 | 1.6 | 6.8
✅ Interpretation:
Mat Width & Depth = Equipment footprint + 0.3 m clearance on all sides.
Perimeter = Total length if you want a walkway mat around the equipment.
136.76 | meters | 150 meters

## MEL
TAG STATUS O - Operational V- Void | WBS | Sector code | Equipment Type | System and sub system code | Sequential Serial Number | Suffix | Equipment Tag | Description | PROCESS OE CODE | OWNER OE CODE | 3D MODEL OE CODE | PARENT TAG | Discipline Code | Equipment Type2 | Operational Arrangement | Continuous or Intermittent | Rated Duty (kW) | Rated Flowrate (m³/h) | Rated Flowrate (MMscfd) | Rated Flowrate (kg/h) | Capacity (m³) | MIN Operating Pressure (barg) | MAX Operating Pressure (barg) | MIN Operating Temperature (°C) | MAX Operating Temperature (°C) | MIN Design Pressure (barg) | MAX Design Pressure (barg) | MIN Design Temperature (°C) | MAX Design Temperature (°C) | Absorbed Electrical Power (kW) | Driver Rated Power (kW) | Emergency Load | Length / T-T (m) | Width / Diameter (m) | Height / T-T (m) | Dry Weight (kg) | Operating Weight (kg) | PFD/UFD Reference | Material | Notes
O | S11 | 70 | VP | 10 | 0001 |  | 70-VP-10-0001 | Inlet Pig Receiver | 2 | 2 | 0 |  | ME | Pig Trap | 1 x 100% | Intermittent | [5 empty] | 53 | 176 | -8 | 90 | FV | 526 | -46 | 105 | N/A | N/A | No | 14 | 18" ID (Minor) & 20" ID (Major) |  | 20800 | 23400 | AZ-AB1-70-SK02-401101 | LTCS + 3mm CA + 316 overlay door seals | Pig Receiver 18" pipeline Note: Hot condensate at 90°C will be used for wax removal at the end of the pigging operation. Weight & Dimension based on preliminary calculation and as per Datasheet.
O | S11 | 70 | VZ | 11 | 1001 |  | 70-VZ-11-1001 | Slug Catcher | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 50% | Continuous |  |  |  | Liq: 222139 Gas: 373456 Aque: 8095 | 675 | 56 | 65 | -12 | 90 | FV | 150 | -35 | 105 | N/A | N/A | No | 130 | 19 |  | 1800000 |  | AZ-AB1-70-SK02-401101 | Inlet: LTCS + 3mm CA Water Outlet: LTCS + 6mm CA Gas Outlet: LTCS + 3mm CA Condensate Outlet: LTCS + 6mm CA Fingers: LTCS + 3mm CA | Finger Type 8 x 48". Dimensions are based on Process calculations, Vendor to Confirm. Overall Linear Length = 130m, including 10m for inlet distribution piping and 120m combined linear finger and manifold length. Overall Width for both Slug Catchers = 42m, including 4m gap between the slug catchers. Dry weight includes 6mm CA for manifolds and all loose fittings, loose pipes, prefabricated spools and manifolds. 675 m³ slug volume Design Code ASME B 31.8 Both slug catchers are in operation (2 x 50%) during normal operation and pigging. Post pigging, one slug catcher taken out of service for wax removal and other slug catcher operating at 100% capacity. Operation repeated for the second slug catcher and then returned to normal operation. Note: Post-pigging, hot condensate at 90°C will be circulated through the slug catcher until the outlet temperature reaches 41°C for wax removal.
O | S11 | 70 | VZ | 11 | 2001 |  | 70-VZ-11-2001 | Slug Catcher | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 50% | Continuous |  |  |  | Liq: 222139 Gas: 373456 Aque: 8095 | 675 | 56 | 65 | -12 | 90 | FV | 150 | -35 | 105 | N/A | N/A | No | 130 | 19 |  | 1800000 |  | AZ-AB1-70-SK02-401101 | Inlet: LTCS + 3mm CA Water Outlet: LTCS + 6mm CA Gas Outlet: LTCS + 3mm CA Condensate Outlet: LTCS + 6mm CA Fingers: LTCS + 3mm CA | Finger Type 8 x 48". Dimensions are based on Process calculations, Vendor to Confirm. Overall Linear Length = 130m, including 10m for inlet distribution piping and 120m combined linear finger and manifold length. Overall Width for both Slug Catchers = 42m, including 4m gap between the slug catchers. Dry weight includes 6mm CA for manifolds and all loose fittings, loose pipes, prefabricated spools and manifolds. 675 m³ slug volume Design Code ASME B 31.8 Both slug catchers are in operation (2 x 50%) during normal operation and pigging. Post pigging, one slug catcher taken out of service for wax removal and other slug catcher operating at 100% capacity. Operation repeated for the second slug catcher and then returned to normal operation. Note: Post-pigging, hot condensate at 90°C will be circulated through the slug catcher until the outlet temperature reaches 41°C for wax removal.
O | S11 | 70 | ES | 20 | 0001 |  | 70-ES-20-0001 | Condensate Heater | 2 | 2 | 0 |  | ME | Shell and Tube Exchanger | 1 x 100% | Continuous | 11373 | 664.5 (Tube) 119.12 (Shell) | 74.47 (Tube) 82.16 (Shell) | 419432 (Tube) 114278 (Shell) | 4.2 (Tube) 6.9 (Shell) | 10.6 (Shell) 54.40 (Tube) | 16 (Shell) 63.40 (Tube) | 65 (Shell) -11.25 (Tube) | 150 (Shell) 50.2 (Tube) | FV | 44 (Shell) 57 (Tube) | -12 (Shell) -46 (Tube) | 165 (Shell) 150 (Tube) | N/A | N/A | No | 8.534 (Tube) 10.7 (Overall) | 1.5 | 2.2 | 32000 | 43000 | AZ-AB1-70-SK02-401101 | Shell: CS + 3mm CA Tubes: 316/316L Tubesheet: CS +3mm CA + 316L Clad Tubeside Channel: LTCS + 3mm CA | No.1 Shell and Tube BEU TEMA Type Weight (dry) includes shell and bundle. Shell ID 1.20m / Tube Length 8.534m. Total Heat Transfer Area 720.14 m2.
O | S11 | 70 | ES | 20 | 0003 | A | 70-ES-20-0003A | Condensate Recycle Heater | 2 | 2 | 0 |  | ME | Shell and Tube Exchanger | 1 x 100% | Intermittent | 2010.2 | 230 (Tube) 42.1 (Shell) | 25.78 (Tube) 29.04 (Shell) | 177850 (Tube) 40395 (Shell) | 0.79 (Tube) 2.1 (Shell) | 10.6 (Shell) 59 (Tube) | 16 (Shell) 54 (Tube) | 65 (Shell) 48.9 (Tube) | 150 (Shell) 90 (Tube) | FV (Shell) FV (Tube) | 52 (Shell) 67 (Tube) | -12 (Shell) -12 (Tube) | 165 (Shell) 105 (Tube) | N/A | N/A | No | 5.0 (Tube) 6.143 (Overall) | 1.0 | 1.7 | 10500 | 13500 | AZ-AB1-70-SK02-401102 | Shell: CS+3mm CA Channel:CS+3mm CA Tubesheet: CS clad 316L Tubeside Tubes:316/316L | No.2 Shell and Tube arranged in series: 70-ES-20-0003 A / B. DEU TEMA Type Weight (dry) includes shell and bundle. Shell ID 0.840m / Tube Length 5m. Heat Transfer Area 208.92 m2 each shell
O | S11 | 70 | ES | 20 | 0003 | B | 70-ES-20-0003B | Condensate Recycle Heater | 2 | 2 | 0 |  | ME | Shell and Tube Exchanger | 1 x 100% | Intermittent | 2010.2 | 230 (Tube) 42.1 (Shell) | 25.78 (Tube) 29.04 (Shell) | 177850 (Tube) 40395 (Shell) | 0.79 (Tube) 2.1 (Shell) | 10.6 (Shell) 59 (Tube) | 16 (Shell) 54 (Tube) | 65 (Shell) 48.9 (Tube) | 150 (Shell) 90 (Tube) | FV (Shell) FV (Tube) | 52 (Shell) 67 (Tube) | -12 (Shell) -12 (Tube) | 165 (Shell) 105 (Tube) | N/A | N/A | No | 5.0 (Tube) 6.143 (Overall) | 1.0 | 1.7 | 10500 | 13500 | AZ-AB1-70-SK02-401102 | Shell: CS+3mm CA Channel:CS+3mm CA Tubesheet: CS clad 316L Tubeside Tubes:316/316L | See Exchanger 70-ES-20-0003A.
O | S20 | 70 | PA | 20 | 0001 | A | 70-PA-20-0001A | Condensate Recycle Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% (see notes) | Continuous |  | 148.2 |  |  |  | 30.02 | 66.96 | 47 | 50 | FV | 74 | -46 | 65 | 216 | 250 | No | 1.0 | 1.0 | 8.8 | 6800 | 7900 | AZ-AB1-70-SK02-401102 | Casing: LTCS +3mm CA Impeller: 12% Cr API 610 (S-6) | Centrifugal (API 610 VS6) 7 stages 2x100% during normal operation but both pumps will run simultaneously during pigging. Main skid dimensions based on Past project reference and motor sizing based on Flowserve online selection tool. Main skid: 1 x 1 x 8.8 m (6,800kg), 5.8m depth, 3m height above ground, 1m x 1m soleplate. Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg)
O | S20 | 70 | PA | 20 | 0001 | B | 70-PA-20-0001B | Condensate Recycle Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% (see notes) | Continuous |  | 148.2 |  |  |  | 30.02 | 66.96 | 47 | 50 | FV | 74 | -46 | 65 | 216 | 250 | No | 1.0 | 1.0 | 8.8 | 6800 | 7900 | AZ-AB1-70-SK02-401102 | Casing: LTCS +3mm CA Impeller: 12% Cr API 610 (S-6) | Centrifugal (API 610 VS6) 7 stages 2x100% during normal operation but both pumps will run simultaneously during pigging. Main skid dimensions based on Past project reference and motor sizing based on Flowserve online selection tool. Main skid: 1 x 1 x 8.8 m (6,800kg), 5.8m depth, 3m height above ground, 1m x 1m soleplate. Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg)
O | S11 | 70 | PA | 20 | 0002 | A | 70-PA-20-0002A | Condensate Recycle Booster Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 230 |  |  |  | 58 | 130.2 | 90 | 90 | FV | 141 | -12 | 105 | 539 | 600 | No | 5.5 | 3.0 | 3.0 | 13500 | 14000 | AZ-AB1-70-SK02-401101 | Casing: CS +3mm CA Impeller: 12% Cr API 610 (S-6) | Centrifugal (API 610 Standard BB5) 7 (+ 1 blank) stages Main skid including seal system: 5.5 x 3.0 x 3.0m (13,500kg) 56.2 bar rated differential pressure Main skid dimensions based on past project similar pumps, and motor sizing based on Sulzer online selection tool.
O | S11 | 70 | PA | 20 | 0002 | B | 70-PA-20-0002B | Condensate Recycle Booster Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 230 |  |  |  | 58 | 130.2 | 90 | 90 | FV | 141 | -12 | 105 | 539 | 600 | No | 5.5 | 3.0 | 3.0 | 13500 | 14000 | AZ-AB1-70-SK02-401101 | Casing: CS +3mm CA Impeller: 12% Cr API 610 (S-6) | Centrifugal (API 610 Standard BB5) 7 (+ 1 blank) stages Main skid including seal system: 5.5 x 3.0 x 3.0m (13,500kg) 56.2 bar rated differential pressure Main skid dimensions based on past project similar pumps, and motor sizing based on Sulzer online selection tool.
O | S11 | 70 | VF | 20 | 0001 |  | 70-VF-20-0001 | Slug Catcher Condensate Filter | 2 | 2 | 0 |  | ME | Filter Unit | 1 x 100% | Continuous |  |  |  | Liq: 237490 Gas: 4455 |  | 55.9 | 64.9 |  |  | FV | 80 | -46 | 105 | N/A | N/A | No | 2.6 | 0.7 | 1.5 | 1000 | 1500 | AZ-AB1-70-SK02-401101 | Shell: LTCS +3mm CA Internals: 316/316L | Basket type filter; 200 microns mesh size Dimensions based on budgetary bid from ASCO FILTI.
O | S11 | 70 | VF | 20 | 0002 |  | 70-VF-20-0002 | Slug Catcher MEG Filter | 2 | 2 | 0 |  | ME | Filter Unit | 1 x 100% | Continuous |  |  |  | Liq: 8100 |  | 55.9 | 64.9 |  |  | FV | 150 | -46 | 60 | N/A | N/A | No | 0.6 | 0.3 | 2.1 (approx.) | 800 | 1200 | AZ-AB1-70-SK02-401101 | Shell: LTCS +3mm CA Internals: 316/316L | Basket type filter; 200 microns mesh size Dimensions based on budgetary bid from ASCO FILTI.
O | S20 | 70 | VZ | 20 | 0001 |  | 70-VZ-20-0001 | HP Separator | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  |  |  | Liq: 418621 Gas: 7898 Aque: 11837 |  | FV | 30 | 45 | 49 | FV | 35 | -46 | 105 | N/A | N/A | No | 9.9 | 3.3 |  | 60000 | 135000 | AZ-AB1-70-SK02-401102 | 316L / LTCS + 316L Clad | Horizontal 2 phase (gas-liquid) separator. Weight and sizes based on PV Elite Calcs and FEED Process data.
O | S20 | 70 | VZ | 20 | 0002 |  | 70-VZ-20-0002 | LP Separator | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  |  |  | Liq: 234104 Gas: 4721 Aque: 693 |  | FV | 9 | 47 | 50 | FV | 17 | -20 | 70 | N/A | N/A | No | 10.55 | 3.5 |  | 41000 | 138000 | AZ-AB1-70-SK02-401102 | 316/316L / CS + 3mm CA + Internal Lining | Horizontal 3 phase separator (internal weir) Or LTCS + Internal Lining + Anodes Weight based on PVElite Calc, Size based on Process FEED data.
O | S20 | 70 | PA | 25 | 0001 | A | 70-PA-25-0001A | Condensate Export Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 310 |  |  |  | 8.97 | 32.57 | 46 | 50 | FV | 42 | -12 | 70 | 220 | 250 | No | 1.1 | 1.1 | 7.5 | 6300 | 7300 | AZ-AB1-70-SK02-401103 | Casing: CS Impeller: 12% Cr API 610 (S6) | Centrifugal API 610 Vertically Suspended type (VS6) Seal API Plan 53B Dimensions, weight, and sizing estimated based on Trillium budgetary bid. Main Skid: 4.1m depth, 3.4m height above grade to top of motor, 1.1m x 1.1m soleplate. Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg)
O | S20 | 70 | PA | 25 | 0001 | B | 70-PA-25-0001B | Condensate Export Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 310 |  |  |  | 8.97 | 32.57 | 46 | 50 | FV | 42 | -12 | 70 | 220 | 250 | No | 1.1 | 1.1 | 7.5 | 6300 | 7300 | AZ-AB1-70-SK02-401103 | Casing: CS Impeller: 12% Cr API 610 (S6) | Centrifugal API 610 Vertically Suspended type (VS6) Seal API Plan 53B Dimensions, weight, and sizing estimated based on Trillium budgetary bid. Main Skid: 4.1m depth, 3.4m height above grade to top of motor, 1.1m x 1.1m soleplate. Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg)
O | S31 | 70 | VP | 25 | 0001 |  | 70-VP-25-0001 | Condensate Export Pig Launcher | 2 | 2 | 0 |  | ME | Pig Trap | 1 x 100% | Intermittent | [6 empty] | 24 |  | 50 | FV | 42 | -12 | 70 | N/A | N/A | No | 3.5 | 12" ID (Minor) & 14" ID (Major) |  | 1100 | 1200 | AZ-AB1-70-SK02-401103 | CS + 3mm CA + 316 Overlay door seals | Pig Launcher 12" pipeline Dimensions based on Ergil Pig Laucher Catalogue data
O | S31 | 70 | UN | 26 | 0001 |  | 70-UN-26-0001 | Condensate Export Metering Package | 2 | 2 | 0 |  | INS | Metering Package | 1 x 100% | Continuous |  | 310 |  |  |  |  | 24.5 |  | 50 | FV | 42 | -12 | 70 |  |  | No | 12 | 5 | 4 | 4600 |  | AZ-AB1-70-SK02-401103 | CS + 3mm CA (VTA) | Metering package with associated liquid hydrocarbon distribution and BS&W analyser.
O | S36 | 70 | HE | 28 | 0001 |  | 70-HE-28-0001 | Closed Drains Drum Heater | 2 | 2 | 0 |  | ME | Electrical Heater | 1 x 100% | Intermittent | 68 |  |  |  |  | FV | 0.01 | -12 | 50 | FV | 9 | -46 | 65 | 68 | 84 | No | 3.6 | 0.2 |  | 180 |  | AZ-AB1-70-SK02-401154 | Sheath (of element): Alloy 625 (VTA) | Electric Heater 1X100% Dimensions and weight based on DFINITI budgetary bid. Does not include the UCP for the heater (2x1.8x1m; 630 kg) Rated Power includes 20% margin on duty Instrument & Electrical tags for 70-HE-28-0001 and 70-PA-28-0001 are duplicated. Make 70-HE-28-0001 unique sequence number in EPSCC stage.
O | S28 | 70 | PA | 28 | 0001 |  | 70-PA-28-0001 | Open Drains Recovered Oil Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 1 x 100% | Intermittent |  | 15 |  |  |  | 0.94 | 13.34 | -12 | 40 | FV | 30 | -12 | 60 | 20.9 | 30 | No | 2.1 | 0.8 (approx.) | 0.6 (approx.) | 1230 | 1460 | AZ-AB1-70-SK02-401155 | Casing: CS + 3mm CA Impeller: 12% Cr API 610 (S6) | Centrifugal Pump ISO 5199 Horizontal Open drains oil pumps and open drains recovered oil pumps to be sized for pump-out in 30 minutes. Dimensions and weight based on Sulzer budgetary bid, motor sizing based on Flowserve selection. Instrument & Electrical tags for 70-HE-28-0001 and 70-PA-28-0001 are duplicated. Make 70-HE-28-0001 unique sequence number in EPSCC stage.
O |  | 70 | PA | 28 | 0007 | A | 70-PA-28-0007A | Closed Drains Pump |  |  |  |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 6.5 |  |  |  | 2.49 | 9.89 | -12 | 50 | FV | 30 | -20 | 65 | 11.3 | 15 | No | 2.5 | 1.6 | 2.8 | 1070 | 1177 | AZ-AB1-70-SK02-401520 | Casing: 316/316L Impeller: 316/316L API 610 (A8) | Centrifugal 2X100% API 610 OH2 Added in Optimise phase due to NPSHA requirements of the Closed Drains Drum Booster Pumps. Dimensions and weights estimated based on Trillium reference. This is an optional pump that may not be required if the complete duty can be selected/handled by the closed drains drum booster pump using a single VS pump with a transportable boot length.
O |  | 70 | PA | 28 | 0007 | B | 70-PA-28-0007B | Closed Drains Pump |  |  |  |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 6.5 |  |  |  | 2.49 | 9.89 | -12 | 50 | FV | 30 | -20 | 65 | 11.3 | 15 | No | 2.5 | 1.6 | 2.8 | 1070 | 1177 | AZ-AB1-70-SK02-401520 | Casing: 316/316L Impeller: 316/316L API 610 (A8) | Centrifugal 2X100% API 610 OH2 Added in Optimise phase due to NPSHA requirements of the Closed Drains Drum Booster Pumps. Dimensions and weights estimated based on Trillium reference. This is an optional pump that may not be required if the complete duty can be selected/handled by the closed drains drum booster pump using a single VS pump with a transportable boot length.
O | S36 | 70 | PS | 28 | 0001 | A | 70-PS-28-0001A | Closed Drains Drum Booster Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 6.5 |  |  |  | 0.08 | 3.21 | -12 | 50 | FV | 17 | -46 | 65 | 1.5 | 4.0 | No | 0.7 | 0.7 | 2.9 | 1530 | 1700 | AZ-AB1-70-SK02-401154 | Casing: 316/316L Impeller: 316/316L API 610 (A8) | Centrifugal API 610 Vertically Suspended type VS1 Dimensions and weight based on Sulzer reference, motor sizing based on Sulzer selection. Closed Drains Drum boot specified as 1.75 m in depth as per recommendation from Mechanical for NPSHA requirements. Maximum operating pressure can be up to 13.0 barg if Closed Drains Pump & Closed Drains Drum Booster Pump are combined into a single duty pump.
O | S36 | 70 | PS | 28 | 0001 | B | 70-PS-28-0001B | Closed Drains Drum Booster Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 6.5 |  |  |  | 0.08 | 3.21 | -12 | 50 | FV | 17 | -46 | 65 | 1.5 | 4.0 | No | 0.7 | 0.7 | 2.9 | 1530 | 1700 | AZ-AB1-70-SK02-401154 | Casing: 316/316L Impeller: 316/316L API 610 (A8) | Centrifugal API 610 Vertically Suspended type VS1 Dimensions and weight based on Sulzer reference, motor sizing based on Sulzer selection. Closed Drains Drum boot specified as 1.75 m in depth as per recommendation from Mechanical for NPSHA requirements. Maximum operating pressure can be up to 13.0 barg if Closed Drains Pump & Closed Drains Drum Booster Pump are combined into a single duty pump.
O | S28 | 70 | PS | 28 | 0003 | A | 70-PS-28-0003A | Open Drains Treatment Oil Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 15 |  |  |  | 0.0 | 2.65 | -12 | 40 |  | 9 | -12 | 60 | 1.46 | 4 | No | 0.7 | 0.7 | 3 | 1490 | 1650 | AZ-AB1-70-SK02-401155 | Casing: CS + 3mm CA Impeller: 12% Cr API 610 (S6) | Centrifugal API 610 Vertically Suspended type VS1/VS4 Open drains oil pumps and open drains recovered oil pumps to be sized for pump-out in 30 minutes. Dimensions and weight based on Trillium budgetary bid, sizing and pump depth based on Flowserve selection. 0.7mx0.7mx3m, 1486kg (1.5m-depth, 1.5m-mount flange to top of motor).
O | S28 | 70 | PS | 28 | 0003 | B | 70-PS-28-0003B | Open Drains Treatment Oil Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 15 |  |  |  | 0.0 | 2.65 | -12 | 40 |  | 9 | -12 | 60 | 1.46 | 4 | No | 0.7 | 0.7 | 3 | 1490 | 1650 | AZ-AB1-70-SK02-401155 | Casing: CS + 3mm CA Impeller: 12% Cr API 610 (S6) | Centrifugal API 610 Vertically Suspended type VS1/VS4 Open drains oil pumps and open drains recovered oil pumps to be sized for pump-out in 30 minutes. Dimensions and weight based on Trillium budgetary bid, sizing and pump depth based on Flowserve selection. 0.7mx0.7mx3m, 1486kg (1.5m-depth, 1.5m-mount flange to top of motor).
O | S28 | 70 | PS | 28 | 0004 | A | 70-PS-28-0004A | Off spec Water Recycle Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 50 |  |  |  | 0.03 | 1.3 | -12 | 40 |  | 9 | -12 | 60 | 3.15 | 5.5 | No | 0.5 | 0.5 | 5.55 | 350 | 390 | AZ-AB1-70-SK02-401155 | Casing: CS + 3mm CA Impeller: 12% Cr API 610 (S6) | Centrifugal API 610 VS1/VS2 type pump. Open drains water pumps and off spec water recycle pumps to be sized for pump-out in 2 hours. Dimensions estimate, weight estimate and electrical ratings based on Flowserve reference. Total Length of 5.555m consists of 3.55m below-grade and 2m above-grade.
O | S28 | 70 | PS | 28 | 0004 | B | 70-PS-28-0004B | Off spec Water Recycle Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 50 |  |  |  | 0.03 | 1.3 | -12 | 40 |  | 9 | -12 | 60 | 3.15 | 5.5 | No | 0.5 | 0.5 | 5.55 | 350 | 390 | AZ-AB1-70-SK02-401155 | Casing: CS + 3mm CA Impeller: 12% Cr API 610 (S6) | Centrifugal API 610 VS1/VS2 type pump. Open drains water pumps and off spec water recycle pumps to be sized for pump-out in 2 hours. Dimensions estimate, weight estimate and electrical ratings based on Flowserve reference. Total Length of 5.555m consists of 3.55m below-grade and 2m above-grade.
O | S28 | 70 | TE | 28 | 0001 |  | 70-TE-28-0001 | Open Drains Treatment Basin | 2 | 2 | 0 |  | CIV | Basin | 1 x 100% | Intermittent |  |  |  |  | 1652 | ATM | ATM | -12 | 40 | -0.0025 | ATM + 4m of Water | -12 | 60 | N/A | N/A | No | 63 | 8 | 5.5 |  |  | AZ-AB1-70-SK02-401155 | Concrete + Internal Lining | Sizing provided by CIVIL.
O | S28 | 70 | TE | 28 | 0002 |  | 70-TE-28-0002 | Observation Basin | 2 | 2 | 0 |  | CIV | Basin | 1 x 100% | Intermittent |  |  |  |  | 302 | ATM | ATM | -12 | 40 | -0.0025 | ATM + 4m of Water | -12 | 60 | N/A | N/A | No | 12 | 8 | 5.5 |  |  | AZ-AB1-70-SK02-401155 | Concrete + Internal Lining | Sizing provided by CIVIL.
O | S28 | 70 | TE | 28 | 0003 |  | 70-TE-28-0003 | Impounding Basin | 2 | 2 | 0 |  | CIV | Basin | 1 x 100% | Intermittent |  |  |  |  | 14872 | ATM | ATM | -12 | 40 | -0.0025 | ATM + 4m of Water | -12 | 60 | N/A | N/A | No | 75.8 | 57 | 5.5 |  |  | AZ-AB1-70-SK02-401155 | Concrete + Internal Lining | Sizing provided by CIVIL.
O | S36 | 70 | VZ | 28 | 0001 |  | 70-VZ-28-0001 | Closed Drains Drum | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Intermittent |  |  |  |  | 36 | FV | 0.01 | -12 | 50 | FV | 9 | -46 | 65 | N/A | N/A | No | 5.0 | 2.3 |  | 12000 |  | AZ-AB1-70-SK02-401154 | LTCS + 3mm CA + Internal Lining | Internal coating shall be in accordance with AZ-AB1-70-SK02-140006. Closed Drains Drum boot specified as 1.75 m in depth as per recommendation from Mechanical for NPSHA requirements.
O | S28 | 70 | VZ | 28 | 0002 |  | 70-VZ-28-0002 | Oil Collection Drum | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Intermittent |  |  |  |  | 30 |  | 0.1 | AMB | 40 | FV | 3.5 | -12 | 60 | N/A | N/A | No | 7.0 | 2.5 |  | 11260 |  | AZ-AB1-70-SK02-401155 | Shell: LTCS + 3mm CA + Internal Coating | Internal coating shall be in accordance with AZ-AB1-70-SK02-140006.
O | S20 | 70 | EA | 31 | 1001 |  | 70-EA-31-1001 | 1st Stage FGC Recycle Cooler | 2 | 2 | 0 |  | ME | Air Cooler | 1 x 100% | Intermittent | 357 | 875.2 (Actual volume flow rate) | 5.7 | 6185 | 0.51 | 8.8 | 9.8 | 45 (Process Outlet) -12 (Air side Inlet) | 145.7 (Process Inlet) | FV | 35 | -46 | 170 | 2.4 (see remarks) | 3x 4 kW (see remarks) | No | 8.8 | 1.6 | 6.8 | 9796 | 10263 | AZ-AB1-70-SK02-401104 | Header: 316/316L Tubes: 316/316L | Air Cooler 1X100%. Forced draft air cooler. 3x50% fans per bay. Shipped to site as semi-assembled module with short legs. 1 bay, 1 bundle, Heat Transfer Area 1136.2 m2. 93 tubes / 31.75mm OD / 6.5m L / Extruded fins. 15kW Electric Heater, 100% Automatic Louvres and 100% AV fans required for winterization.
O | S20 | 70 | EA | 31 | 1002 |  | 70-EA-31-1002 | 2nd Stage FGC Suction Cooler | 2 | 2 | 0 |  | ME | Air Cooler | 1 x 100% | Continuous | 417.5 | 668.9 (Actual volume flow rate) | 14.17 | 14720 | 0.69 | 28.5 | 29 | 45 (Process Outlet) -12 (Air side Inlet) | 109.9 (Process Inlet) | FV | 47 | -46 | 155 | 5.4 (see remarks) | 3x 4 kW (see remarks) | No | 8.8 | 2.3 | 6.8 | 13065 | 13685 | AZ-AB1-70-SK02-401104 | Header: 316/316L Tubes: 316/316L | Air Cooler 1X100%. Forced draft air cooler. 3x50% fans per bay. Shipped to site as semi-assembled module with short legs. 1 bay, 1 bundle. Heat Transfer Area 1798.3 m2. 145 tubes / 31.75mm OD / 6.5m L / Extruded fins. 25kW Electric Heater, 100% Automatic Louvers and 100% AV fans required for winterization.
O | S31 | 70 | EA | 31 | 1004 |  | 70-EA-31-1004 | Export Compressor Aftercooler | 2 | 2 | 0 |  | ME | Air Cooler | 2 x 50% | Continuous | 5031 | 3032.2 (Actual volume flow rate) | 225 | 193852 | 4.06 | 92.4 | 94.4 | 41.7 (Process Outlet) -12 (Air side Inlet) | 92.1 (Process Inlet) | FV | 110 | -46 | 125 | 94.2 (see remarks) | 6x 22kW (see remarks) | No | 13.5 (See notes) | 4.8 (see notes) | 7.1 (See notes) | 84268 | 88326 | AZ-AB1-70-SK02-401106 | Header: LTCS + 3mm CA Tubes: 316/316L | Air Cooler 1X100% per export compressor. Forced draft air cooler. 3 fans per bay, 2 bays per equipment tag (fans 5xrunning +1xstandby). Shipped as loose parts for site-assembly. Provided dimensions are for 1 bay only, and estimated based on internal sizing tool. 0.5m minimum spacing considered between adjacent bays. 2-bays, 2 bundles per bay. Heat Transfer. Area 14288 m2. 198 tubes per bundle / 25.4mm OD / 11m L/ Extruded fins. No winterisation required.
O | S20 | 70 | EA | 31 | 2001 |  | 70-EA-31-2001 | 1st Stage FGC Recycle Cooler | 2 | 2 | 0 |  | ME | Air Cooler | 1 x 100% | Intermittent | 357 | 875.2 (Actual volume flow rate) | 5.7 | 6185 | 0.51 | 8.8 | 9.8 | 45 (Process Outlet) -12 (Air side Inlet) | 145.7 (Process Inlet) | FV | 35 | -46 | 170 | 2.4 (see remarks) | 3x 4 kW (see remarks) | No | 8.8 | 1.6 | 6.8 | 9796 | 10263 | AZ-AB1-70-SK02-401104 | Header: 316/316L Tubes: 316/316L | Identical to Train 1.
O | S20 | 70 | EA | 31 | 2002 |  | 70-EA-31-2002 | 2nd Stage FGC Suction Cooler | 2 | 2 | 0 |  | ME | Air Cooler | 1 x 100% | Continuous | 417.5 | 668.9 (Actual volume flow rate) | 14.17 | 14720 | 0.69 | 28.5 | 29 | 45 (Process Outlet) -12 (Air side Inlet) | 109.9 (Process Inlet) | FV | 47 | -46 | 155 | 5.4 (see remarks) | 3x 4 kW (see remarks) | No | 8.8 | 2.3 | 6.8 | 13065 | 13685 | AZ-AB1-70-SK02-401104 | Header: 316/316L Tubes: 316/316L | Identical to Train 1.
O | S31 | 70 | EA | 31 | 2004 |  | 70-EA-31-2004 | Export Compressor Aftercooler | 2 | 2 | 0 |  | ME | Air Cooler | 2 x 50% | Continuous | 5031 | 3032.2 (Actual volume flow rate) | 225 | 193852 | 4.06 | 92.4 | 94.4 | 41.7 (Process Outlet) -12 (Air side Inlet) | 92.1 (Process Inlet) | FV | 110 | -46 | 125 | 94.2 (see remarks) | 6x 22kW (see remarks) | No | 13.5 (See notes) | 4.8 (see notes) | 7.1 (See notes) | 84268 | 88326 | AZ-AB1-70-SK02-401106 | Header: LTCS + 3mm CA Tubes: 316L | Identical to Train 1.
O | S20 | 70 | KA | 31 | 1001 |  | 70-KA-31-1001 | 1st Stage Flash Gas Compressor | 2 | 2 | 0 |  | ME | Reciprocating Compressor | 2 x 100% | Continuous | 430.9 (Shaft Power, PSV relief) | 6310.9 (Normal m3/h) (Suction) | 5.7 | 6185 |  | 8.7 (Suction) | 29 (Discharge) | Suction: 45.8 Discharge: 142.2 | Suction: 47 Discharge: 150 | FV | 35 | -46 | 170 | 1044 | 1500 | No | 9.0 | 7.0 | 4.3 | 40000 | 42000 | AZ-AB1-70-SK02-401104 | LTCS Cylinder/Pistons and Liner (VTA) | Electric Drive Common crankshaft with Second Stage (same compressor casing and motor) API Standard 618 Motor-driven reciprocating compressor together with associated ancillaries and control systems (compressor, driver, seal & lube oil system, LCP), suction and discharge pulsation dampers. Minimum 3-step capacity control (0-50-100%) with variable volume clearance pocket and recycling as required. Interstage Coolers and Scrubbers are not part of vendor scope. Overall footprint dimensions estimated from Neuman and Esser budgetary bid for water cooled reciprocating compressor. Weight pro-rated based on the conservative Burckhardt revised bid. Possibility of splitting into multiple skids for transportation. Lube Oil and Jacket Water Cooler skid: 2.4m x 1.6m x 1m. Control skid (valve unloading, gauge board etc.): 1.6m x 1.6m x 1m. Motor sizing based on internal estimate.
O | S20 | 70 | KA | 31 | 1002 |  | 70-KA-31-1002 | 2nd Stage Flash Gas Compressor | 2 | 2 | 0 |  | ME | Reciprocating Compressor | 2 x 100% | Continuous | 613.3 (Shaft Power, PSV relief) | 15811.5 (Normal m3/h) (Suction) | 14.2 | 14716 |  | 28.4 (Suction) | 54.9 (Discharge) | Suction: 45 Discharge: 100.8 | Suction: 45 Discharge: 103.4 | FV | 65 | -46 | 120 | Included in 1st stage data | Included in 1st stage data | No | Included in 1st stage data | Included in 1st stage data | Included in 1st stage data | Included in 1st stage data | Included in 1st stage data | AZ-AB1-70-SK02-401104 | LTCS Cylinder/Pistons and Liner (VTA) | Included in 1st stage data
O | S31 | 70 | KA | 31 | 1003 |  | 70-KA-31-1003 | Export Compressor | 2 | 2 | 0 |  | ME | Centrifugal Compressor | 2 x 50% | Continuous | 6463 (Shaft power) | 5172.73 (Actual m3/h) (Suction) | 247.5 | 213237.2 |  | 37.5 (Suction) | 94.4 (Discharge) | Suction: -16.3 Discharge: 42.0 | Suction: 12.5 Discharge: 92.1 | FV | 110 | -46 | 125 | 7109 | 8000 | No | 12.8 | 4.65 | 6.75 | 68359 |  | AZ-AB1-70-SK02-401106 | LTCS (VTA) | Rated Duty and Flow values are from HMB Case 1 with 10% additional flow margin for Slug Flow (247.5 MMSCFD). Rated Duty and absorbed electrical power is based on Siemens shaft power. 2x 50% Trains (1 and 2). Hermetically sealed integrated motor compressor. [HOLD 5] Alternative compact Moto compressor footprint and weight selection is available. Suitability of the technology type has to be confirmed during FEED Phase . Vendor to supply 2x50% VSD motor-driven centrifugal compressors together with associated ancillaries and control systems. including AMB control panels, UCP, VFD, VFD Cooler and Transformer. The normal operating point / guarantee point of each export compressor is 225 mmscfd (total 450 mmscfd). During normal operation, 225 mmscfd is exported to DGN and 225 mmscfd is exported to SCP via 1x50% export compressor. Rated point is 247.5 mmscfd (10% additional slug flow design margin) for each compressor motor sizing. Main compressor skid dimensions and weight based on Siemens budgetary bid for conventional centrifugal compressor: 10 x 5.2 x 3.4m (92,500kg). Auxiliary system dimensions and weight estimated based on past project Siemens reference: Lube oil skid: 4.0 x 2.0 x 4.2m (Wet - 10,776kg) Lube oil air cooler: 9.5 x 2.0 x 4m Lube oil rundown tank: 1.0 x 1.0 x 1.8m (700kg) VFD (in E-House) : 12.8 x 4.3 x 5.8m (10,000kg)
O | S20 | 70 | KA | 31 | 2001 |  | 70-KA-31-2001 | 1st Stage Flash Gas Compressor | 2 | 2 | 0 |  | ME | Reciprocating Compressor | 2 x 100% | Continuous | 430.9 (Shaft Power, PSV relief) | 6310.9 (Normal m3/h) (Suction) | 5.7 | 6185 |  | 8.7 (Suction) | 29 (Discharge) | Suction: 45.8 Discharge: 142.2 | Suction: 47 Discharge: 150 | FV | 35 | -46 | 170 | 1044 | 1500 | No | 9.0 | 7.0 | 4.3 | 40000 | 42000 | AZ-AB1-70-SK02-401104 | LTCS Cylinder/Pistons and Liner (VTA) | Electric Drive Common crankshaft with Second Stage (same compressor casing and motor) API Standard 618 Motor-driven reciprocating compressor together with associated ancillaries and control systems (compressor, driver, seal & lube oil system, LCP), suction and discharge pulsation dampers. Minimum 3-step capacity control (0-50-100%) with variable volume clearance pocket and recycling as required. Interstage Coolers and Scrubbers are not part of vendor scope. Overall footprint dimensions estimated from Neuman and Esser budgetary bid for water cooled reciprocating compressor. Weight pro-rated based on the conservative Burckhardt revised bid. Possibility of splitting into multiple skids for transportation. Lube Oil and Jacket Water Cooler skid: 2.4m x 1.6m x 1m. Control skid (valve unloading, gauge board etc.): 1.6m x 1.6m x 1m. Motor sizing based on internal estimate.
O | S20 | 70 | KA | 31 | 2002 |  | 70-KA-31-2002 | 2nd Stage Flash Gas Compressor | 2 | 2 | 0 |  | ME | Reciprocating Compressor | 2 x 100% | Continuous | 613.3 (Shaft Power, PSV relief) | 15811.5 (Normal m3/h) (Suction) | 14.2 | 14716 |  | 28.4 (Suction) | 54.9 (Discharge) | Suction: 45 Discharge: 100.8 | Suction: 45 Discharge: 103.4 | FV | 65 | -46 | 120 | Included in 1st stage data | Included in 1st stage data | No | Included in 1st stage data | Included in 1st stage data | Included in 1st stage data | Included in 1st stage data | Included in 1st stage data | AZ-AB1-70-SK02-401104 | LTCS Cylinder/Pistons and Liner (VTA) | Included in 1st stage data
O | S31 | 70 | KA | 31 | 2003 |  | 70-KA-31-2003 | Export Compressor | 2 | 2 | 0 |  | ME | Centrifugal Compressor | 2 x 50% | Continuous | 6463 (Shaft power) | 5172.73 (Actual m3/h) (Suction) | 247.5 | 213237.2 |  | 37.5 (Suction) | 94.4 (Discharge) | Suction: -16.3 Discharge: 42.0 | Suction: 12.5 Discharge: 92.1 | FV | 110 | -46 | 125 | 7109 | 8000 | No | 12.8 | 4.65 | 6.75 | 68359 |  | AZ-AB1-70-SK02-401106 | LTCS (VTA) | Identical to Train 1.
O | S20 | 70 | PC | 31 | 1003 |  | 70-PC-31-1003 | 1st Stage FGC Suction Scrubber Pump | 2 | 2 | 0 |  | ME | Rotating Displacement Pumps | 1 x 100% | Intermittent |  | 0.8 |  |  |  | 8.89 | 10.21 | 45 | 47 | FV | 35 | -46 | 155 | 0.032 | 0.75 | No | 2 | 1 | 1 | 500 | 550 | AZ-AB1-70-SK02-401104 | Cylinder: 316/316L Piston:316/316L | Progressive Cavity Pump Dimensions, weights, and sizing estimated from PCM Series A catalogue - Model 3A12 reference. The motor tags and instrument tags for 70-PC-31-1003 and 70-KA-31-1003 are duplicated. Make 70-PC-31-1003 1st Stage FGC Suction Scrubber Pump unique sequence number in EPSCC stage.
O | S20 | 70 | PC | 31 | 2003 |  | 70-PC-31-2003 | 1st Stage FGC Suction Scrubber Pump | 2 | 2 | 0 |  | ME | Rotating Displacement Pumps | 1 x 100% | Intermittent |  | 0.8 |  |  |  | 8.89 | 10.21 | 45 | 47 | FV | 35 | -46 | 155 | 0.032 | 0.75 | No | 2 | 1 | 1 | 500 | 550 | AZ-AB1-70-SK02-401104 | Cylinder: 316/316L Piston:316/316L | Identical to Train 1. The motor tags and instrument tags for 70-PC-31-2003 and 70-KA-31-2003 are duplicated. Make 70-PC-31-2003 1st Stage FGC Suction Scrubber Pump unique sequence number in EPSCC stage
O | S20 | 70 | VZ | 31 | 1001 |  | 70-VZ-31-1001 | 1st Stage FGC Suction Scrubber | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 100% | Continuous |  | 813.6 (Design) |  | 6803.5 (Design) | 0.39 (Working) | 8.7 | 8.7 | 46 | 47 | FV | 35 | -46 | 155 | N/A | N/A | No |  | 0.75 | 2.85 | 482 |  | AZ-AB1-70-SK02-401104 | Shell: 316/316L Internals : 316/316L | Vertical Separator (with demister) Total working volume (to HHLL) = 0.39 m3 Total vessel volume = 1.15 m3 Sizing based on process data. Weight based on PVElite calculations.
O | S20 | 70 | VZ | 31 | 1002 |  | 70-VZ-31-1002 | 2nd Stage FGC Suction Scrubber | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 100% | Continuous |  | 636.7 (Design) |  | 16187.6 (Design) | 0.39 (Working) | 28.4 | 28.4 | 45 | 45 | FV | 47 | -46 | 120 | N/A | N/A | No |  | 0.75 | 2.85 | 773 |  | AZ-AB1-70-SK02-401104 | Shell: 316/316L Internals : 316/316L | Vertical Separator (with demister) Total working volume (to HHLL) = 0.39 m3 Total vessel volume = 1.15 m3 Sizing based on process data. Weight based on PVElite calculations.
O | S20 | 70 | VZ | 31 | 2001 |  | 70-VZ-31-2001 | 1st Stage FGC Suction Scrubber | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 100% | Continuous |  | 813.6 (Design) |  | 6803.5 (Design) | 0.39 (Working) | 8.7 | 8.7 | 46 | 47 | FV | 35 | -46 | 155 | N/A | N/A | No |  | 0.75 | 2.85 | 482 |  | AZ-AB1-70-SK02-401104 | Shell: 316/316L Internals : 316/316L | Identical to Train 1.
O | S20 | 70 | VZ | 31 | 2002 |  | 70-VZ-31-2002 | 2nd Stage FGC Suction Scrubber | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 100% | Continuous |  | 636.7 (Design) |  | 16187.6 (Design) | 0.39 (Working) | 28.4 | 28.4 | 45 | 45 | FV | 47 | -46 | 120 | N/A | N/A | No |  | 0.75 | 2.85 | 773 |  | AZ-AB1-70-SK02-401104 | Shell: 316/316L Internals : 316/316L | Identical to Train 1.
O | S31 | 70 | VZ | 31 | 1003 |  | 70-VZ-31-1003 | Export Compressor Suction Scrubber | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 50% | Continuous |  | 5167.4 (Design) | 247.5 | 213237.2 (Design) | 5.2 (Working) | 37.5 | 48.7 | -16 | 13 | FV | 81 | -46 | 110 | N/A | N/A | No |  | 2.4 | 4.65 | 31250 |  | AZ-AB1-70-SK02-401106 | Shell: LTCS + 3mm CA Internals : 316L | Vertical Separator (with demister) Total working volume (to HHLL) = 5.2 m3 Total vessel volume = 24.66 m3 Sizing based on process data. Weight based on PVElite calculations.
O | S31 | 70 | VZ | 31 | 2003 |  | 70-VZ-31-2003 | Export Compressor Suction Scrubber | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 50% | Continuous |  | 5167.4 (Design) | 247.5 | 213237.2 (Design) | 5.2 (Working) | 37.5 | 48.7 | -16 | 13 | FV | 81 | -46 | 110 | N/A | N/A | No |  | 2.4 | 4.65 | 31250 |  | AZ-AB1-70-SK02-401106 | Shell: LTCS + 3mm CA Internals : 316L | Identical to Train 1.
O | S31 | 70 | ES | 32 | 0001 | A | 70-ES-32-0001A | Gas/Gas Exchanger | 2 | 2 | 0 |  | ME | Shell and Tube Exchanger | 2 x 50% | Continuous | 3666 | 4154.5 (Tube) 4044.5 (Shell) | 225.95 (Tube) 225.4 (Shell) | 195704 (Tube) 194186 (Shell) | 30.4 (Tube) 34.5 (Shell) | 53.4 (Tube) 38 (Shell) | 54.4 (Tube) 47.1 (Shell) | -10.8 (Tube) -17.9 (Shell) | 15 (Tube) 8.7(Shell) | FV | 65 | -46 | 60 | N/A | N/A | No | 14.5 (Tube) 20.0 (Overall) | 3.3 | 3.4 | 185000 | 255000 | AZ-AB1-70-SK02-401105 | Shell: LTCS + 3mm CA Tubes: 316/316L Tubesheet: LTCS +3mm CA +316L Clad Tubeside Channel: LTCS + 3mm CA | Shell and Tube (BEN TEMA Type) Two Shell Arrangement of 70-ES-32-0001A/B is 1 series 2 parallel Weight (dry) includes shell and bundle. Shell ID 2.3m / Tube length 14.5m. Tube quantity= 5713 Nos per exchanger. Heat Transfer Area 4792 m2 each shell (Total 9584 m2).
O | S31 | 70 | ES | 32 | 0001 | B | 70-ES-32-0001B | Gas/Gas Exchanger | 2 | 2 | 0 |  | ME | Shell and Tube Exchanger | 2 x 50% | Continuous | 3666 | 4154.5 (Tube) 4044.5 (Shell) | 225.95 (Tube) 225.4 (Shell) | 195704 (Tube) 194186 (Shell) | 30.4 (Tube) 34.5 (Shell) | 53.4 (Tube) 38 (Shell) | 54.4 (Tube) 47.1 (Shell) | -10.8 (Tube) -17.9 (Shell) | 15 (Tube) 8.7 (Shell) | FV | 65 | -46 | 60 | N/A | N/A | No | 14.5 (Tube) 20.0 (Overall) | 3.3 | 3.4 | 185000 | 255000 | AZ-AB1-70-SK02-401105 | Shell: LTCS + 3mm CA Tubes: 316/316L Tubesheet: LTCS +3mm CA +316L Clad Tubeside Channel: LTCS + 3mm CA | See Exchanger 70-ES-32-0001A
O | S31 | 70 | KT | 32 | 0001A |  | 70-KT-32-0001A | Turbo Expander / Recompressor Package | 2 | 2 |  | 70-KT-32-0001 | ME | Turboexpander | 1 x 100% | Continuous | 1150 (Produced Shaft Power) | 8018.3 (Actual) (Suction) | 496.23 | 428349 |  | 46.95 (Discharge) | 53.3 (Suction) | -17.6 (Discharge) | -9.4 (Suction) | FV | 65 | -46 | 60 | N/A | N/A | No | 5.6 [See notes] | 3.7 [See notes] | 3.2 [See notes] | 23000 | 25000 | AZ-AB1-70-SK02-401105 | LTCS - Compressor 316/316L - Expander (VTA) | Turbo Expander - Recompressor scope includes machine casing, rotating assembly, AMB, thrust bearing together with associated ancillaries and control system including AMB control panels, PLC. Dimensions, weight, and sizing are based on Cryostar bid: Main package baseplate: 5.6m x 3.7m x 3.2m (23,000 kg) AMB Control Cabinet: 2.0m x 1.6m x 0.8m (700 kg) UCP Cabinet: 2.0m x 1.6m x 0.8m (700 kg) Rated duty = design duty is 495 MMSCFD (10% slug flow margin).
O | S31 | 70 | KT | 32 | 0001B |  | 70-KT-32-0001B | Turbo Expander / Recompressor Package | 2 | 2 |  | 70-KT-32-0001 | ME | Recompressor | 1 x 100% | Continuous | 1092.3 (Shaft Power) | 10647.9 (Actual) (Suction) | 495.83 | 427208.1 |  | 45.85 (Suction) | 49.2 (Discharge) | Suction: -17.5 Discharge: -12.4 | Suction: 7.9 Discharge: 12.8 | FV | 65 | -46 | 60 | N/A | N/A | No | Included in 70-KT-32-0001A | Included in 70-KT-32-0001A | Included in 70-KT-32-0001A | Included in 70-KT-32-0001A | Included in 70-KT-32-0001A | AZ-AB1-70-SK02-401105 | LTCS - Compressor 316/316L - Expander (VTA) | Included in 70-KT-32-0001A
O | S31 | 70 | VZ | 32 | 0001 |  | 70-VZ-32-0001 | Inlet Separator | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  | 9120.1 (Design) |  | 431971.4 (Design) | 13.7 (Working) | 54.4 | 54.4 | -8 | 15 | FV | 65 | -46 | 60 | N/A | N/A | No |  | 3.6 | 6.45 | 94500 |  | AZ-AB1-70-SK02-401105 | Shell: LTCS + 3mm CA + Clad 316L in lower wet areas Internals: 316/316L | Vertical Separator with demister. Sizing based on process data. Weight based on PVElite calculations.
O | S31 | 70 | VZ | 32 | 0002 |  | 70-VZ-32-0002 | Turbo Expander Suction Scrubber | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  | 8004.7 (Design) |  | 430547.3 (Design) | 14.7 (Working) | 53.3 | 53.3 | -11 | -9 | FV | 65 | -46 | 60 | N/A | N/A | No |  | 3.7 | 6.6 | 87600 |  | AZ-AB1-70-SK02-401105 | Shell: LTCS + 3mm CA Internals: 316/316L | Vertical Separator with Axial Cyclonic device and demister Total working volume (to HHLL) = 14.69 m3 Total vessel volume = 84.22 m3 Sizing based on process data. Weight based on PVElite calculations.
O | S31 | 70 | VZ | 32 | 0003 |  | 70-VZ-32-0003 | Low Temperature Separator | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  | 8885.8 (Design) |  | 428349.2 (Design) | 17.8 (Working) | 39.1 | 47.1 | -18 | -16 | FV | 65 | -115 | 60 | N/A | N/A | No |  | 4 | 7.05 | 109560 |  | AZ-AB1-70-SK02-401105 | 316/316L | Vertical Separator with Axial Cyclonic device and demister Total working volume (to HHLL) = 17.8 m3 Total vessel volume = 105.35 m3 Sizing based on process data. Weight based on PVElite calculations.
O | S31 | 70 | ES | 35 | 0003 |  | 70-ES-35-0003 | DGN Export Heater | 2 | 2 | 0 |  | ME | Shell and Tube Exchanger | 1 x 100% | Intermittent | 3870 | 3986 (Tube) | 225 (Tube) | 192703 (Tube) 44116 (Shell) | 1.66 (Tube) 1.44 (Shell) | 10.6 (Shell) 44.7 (Tube) | 11.6 (Shell) 45.7 (Tube) | 65 (Shell) -14.41 (Tube) | 150 (Shell) 15.7 (Tube) | FV (Shell) FV (Tube) | 65 (Tube) 50 (Shell) | -46 | 150 (Tube) 165 (Shell) | N/A | N/A | No | 1.829 (Tube) 3.9 (Overall) | 1.1 | 1.94 | 9000 | 12500 | AZ-AB1-70-SK02-401106 | Shell: LTCS + 3mm CA Channel: LTCS + 3mm CA Tubesheet: LTCS +316L Clad Tubeside Tubes: 316L | No.1 Shell and Tube BEU TEMA Type Weight (dry) includes shell and bundle. Shell ID 0.98m / Tube length 1.829m. Heat Transfer Area 99.72 m2.
O | S31 | 70 | HE | 35 | 0001 |  | 70-HE-35-0001 | Start-Up Gas Heater | 2 | 2 | 0 |  | ME | Electrical Heater | 1 x 100% | Intermittent | 525 |  |  | 17232 |  |  | 91.9 | -12 | 20 | FV | 110 | -46 | 65 | 530 | 636 | No | 3.5 | 0.8 |  | 800 |  | AZ-AB1-70-SK02-401106 | Shell: LTCS + 3mm CA Sheath: 316L | Electric Heater 1X100% Rated Power includes 20% margin on duty Dimensions and weight estimated based on past project reference and DFINITI budgetary bid.
O | S31 | 70 | UN | 35 | 0002 |  | 70-UN-35-0002 | SCP Export Metering Package | 2 | 2 | 0 |  | INS | Metering Package | 1 x 100% | Continuous |  |  | 495 |  |  | 91.9 | 93.6 | 42 | 50 | FV | 110 | -46 | 110 |  |  | No | 18 | 5 | 4 | 44000 |  | AZ-AB1-70-SK02-401106 | LTCS + 3mm CA
O | S31 | 70 | UN | 35 | 0003 |  | 70-UN-35-0003 | DGN Export Metering Package | 2 | 2 | 0 |  | INS | Metering Package | 1 x 100% | Continuous |  |  | 495 |  |  | 45.2 | 89.2 | 15.7 | 43.6 | FV | 110 | -46 | 150 |  |  | No | 16 | 5 | 4 | 52000 |  | AZ-AB1-70-SK02-401106 | LTCS + 3mm CA
O | S31 | 70 | UN | 35 | 0004 |  | 70-UN-35-0004 | Buy-back Gas Metering Package | 2 | 2 | 0 |  | INS | Metering Package | 1 x 100% | Intermittent |  |  | 30 |  |  | 90.2 | 91.9 | 41 | 50 | FV | 110 | -46 | 65 |  |  | No | 8 | 3 | 4 | 15000 |  | AZ-AB1-70-SK02-401106 | LTCS + 3mm CA
O | S36 | 70 | FH | 36 | 0001 |  | 70-FH-36-0001 | HP Flare Stack and Tip Package | 2 | 2 | 0 |  | ME | Flare | 1 x 100% | Intermittent |  |  |  | 561830 |  | 0.1 | 4 | -100 | 150 | FV | 15 | -115 | 165 |  |  | No | 75 [See notes] | 30" ID (approx.) | 90 (approx.) | 3200 |  | AZ-AB1-70-SK02-401150 | Stack Pipe: 316/316L Stack Structure: CS Tip: 310S (VTC) | Flame to be monitored with infrared monitoring system. Package to be provided with remote methane detection for monitoring unburnt methane fraction at the flare tip. Common structure for Flare stack for LP and HP. Dimensions based on Zeeco budgetary bid - installed with stack package. Deadman anchors located 75m from centre of stack base. Package is continuously receiving purge gas - rated flowrate represents maximum relieving case which will be intermittent.
O | S36 | 70 | FL | 36 | 0001 |  | 70-FL-36-0001 | LP Flare Stack and Tip Package | 2 | 2 | 0 |  | ME | Flare | 1 x 100% | Intermittent |  |  |  | 17946 |  | 0.01 | 0.1 | -12 | 114 (VTA) | FV | 9 | -46 | 130 (VTA) |  |  | No | 75 [See notes] | 20" ID (approx.) | 90 (approx.) | < 1000 (VTA) |  | AZ-AB1-70-SK02-401152 | Stack Pipe: LTCS + 3mm CA+ Coating as per Project Spec. Stack Structure: CS Tip: 310S (VTC) | Vendor to advise weight (< 1 tonne estimated) Flame to be monitored with infrared monitoring system. Requirement of fuel gas for assisted combustion for low calorific value releases to be confirmed by vendor. Package to be provided with remote methane detection for monitoring unburnt methane fraction at the flare tip. Common structure for Flare stack for LP and HP. Dimensions based on Zeeco budgetary bid - installed with stack package. Deadman anchors located 75m from centre of stack base. Package is continuously receiving purge gas - rated flowrate represents maximum relieving case which will be intermittent.
O | S36 | 70 | HE | 36 | 0002 | A | 70-HE-36-0002A | HP Flare KO Drum A Heater A | 2 | 2 | 0 |  | ME | Electrical Heater | 2 x 50% | Intermittent | 272 | [5 empty] | 0.1 | -12 | 150 | FV | 15 | -20 | 165 | 272 | 450 | No | 5 | 0.5 |  | 550 |  | AZ-AB1-70-SK02-401150 | Sheath (of Element): 316L | Electric Heater is independent for each KO Drum so heats half the total contents each, 2X50%. Dimensions and weight based on DFINITI budgetary bid. Rated Power includes 20% margin on duty
O | S36 | 70 | HE | 36 | 0002 | B | 70-HE-36-0002B | HP Flare KO Drum A Heater B | 2 | 2 | 0 |  | ME | Electrical Heater | 2 x 50% | Intermittent | 272 | [5 empty] | 0.1 | -12 | 150 | FV | 15 | -20 | 165 | 272 | 450 | Yes | 5 | 0.5 |  | 550 |  | AZ-AB1-70-SK02-401150 | Sheath (of Element): 316L | Electric Heater is independent for each KO Drum so heats half the total contents each, 2X50%. Dimensions and weight based on DFINITI budgetary bid. Rated Power includes 20% margin on duty
O | S36 | 70 | HE | 36 | 0003 |  | 70-HE-36-0003 | LP Flare KO Drum Heater | 2 | 2 | 0 |  | ME | Electrical Heater | 1 x 100% | Intermittent | 266 |  |  |  |  | 0.01 |  | -12 | 114 | FV | 9 | -20 | 130 | 266 | 320 | Yes | 4.5 | 0.3 |  | 420 |  | AZ-AB1-70-SK02-401152 | Sheath (of Element): 316/316L (VTA) | Electric Heater 1x100% Dimensions and weight estimated based on DFINITI budgetary bid. Does not include the UCP for the heater (2x1.8x1m; 630 kg) Rated Power includes 20% margin on duty
O | S36 | 70 | HE | 36 | 0005 | A | 70-HE-36-0005A | HP Flare KO Drum B Heater A | 2 | 2 | 0 |  | ME | Electrical Heater | 2 x 50% | Intermittent | 272 | [5 empty] | 0.1 | -12 | 150 | FV | 15 | -20 | 165 | 272 | 365 | No | 3.6 | 0.2 |  | 180 |  | AZ-AB1-70-SK02-401150 | Sheath (of Element): 316L | Electric Heater is independent for each KO Drum so heats half the total contents each, 2X50%. Dimensions and weight based on DFINITI budgetary bid. Rated Power includes 20% margin on duty
O | S36 | 70 | HE | 36 | 0005 | B | 70-HE-36-0005B | HP Flare KO Drum B Heater B | 2 | 2 | 0 |  | ME | Electrical Heater | 2 x 50% | Intermittent | 272 | [5 empty] | 0.1 | -12 | 150 | FV | 15 | -20 | 165 | 272 | 365 | Yes | 3.6 | 0.2 |  | 180 |  | AZ-AB1-70-SK02-401150 | Sheath (of Element): 316L | Electric Heater is independent for each KO Drum so heats half the total contents each, 2X50%. Dimensions and weight based on DFINITI budgetary bid. Rated Power includes 20% margin on duty
O | S36 | 70 | PA | 36 | 0001 | A | 70-PA-36-0001A | HP Flare KO Drum Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 30 |  |  |  | 0.29 | 10.16 | -12 | 41 | FV | 30 | -20 | 60 | 14.7 | 18.5 | Yes | 0.9 | 0.9 | 4.8 | 1400 | 1540 | AZ-AB1-70-SK02-401150 | Casing: 316/316L Impeller:316/316L API 610 (A8) | Centrifugal API standard 610 VS6 type 18 stage Pumps provided with low temperature inhibits to ensure pumps and downstream system are kept within design temperature limits. Dimensions and weight are estimated based on Flowserve reference and past projects. NPSH margin, to be evaluated further. Additional Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg)
O | S36 | 70 | PA | 36 | 0001 | B | 70-PA-36-0001B | HP Flare KO Drum Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 30 |  |  |  | 0.29 | 10.16 | -12 | 41 | FV | 30 | -20 | 60 | 14.7 | 18.5 | No | 0.9 | 0.9 | 4.8 | 1400 | 1540 | AZ-AB1-70-SK02-401150 | Casing: 316/316L Impeller: 316/316L API 610 (A8) | Centrifugal API standard 610 VS6 type 18 stage Pumps provided with low temperature inhibits to ensure pumps and downstream system are kept within design temperature limits. Dimensions and weight are estimated based on Flowserve reference and past projects. NPSH margin, to be evaluated further. Additional Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg)
O | S36 | 70 | PA | 36 | 0004 | A | 70-PA-36-0004A | LP Flare KO Drum Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 11.31 |  |  |  | 0.2 | 10.01 | -12 | 41 | FV | 30 | -20 | 60 | 5.4 | 7.5 | Yes | 0.5 | 0.5 | 3.9 | 1100 | 1210 | AZ-AB1-70-SK02-401152 | Casing: LTCS Impeller: SS316L | Centrifugal API Standard 610 VS6 type Pump capacity to be specified to allow ko drum to be drained from LSHH to LAL in 2 hours. Dimensions estimated and electrical rating based on Flowserve reference. Total height of 3.9m consists of 1.9m below ground, 2m above ground. Additional Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg) Weights estimated based on Trillium reference.
O | S36 | 70 | PA | 36 | 0004 | B | 70-PA-36-0004B | LP Flare KO Drum Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Intermittent |  | 11.31 |  |  |  | 0.2 | 10.01 | -12 | 41 | FV | 30 | -20 | 60 | 5.4 | 7.5 | No | 0.5 | 0.5 | 3.9 | 1100 | 1210 | AZ-AB1-70-SK02-401152 | Casing: LTCS Impeller: SS316L | Centrifugal API Standard 610 VS6 type Pump capacity to be specified to allow ko drum to be drained from LSHH to LAL in 2 hours. Dimensions estimated and electrical rating based on Flowserve reference. Total height of 3.9m consists of 1.9m below ground, 2m above ground. Additional Seal API Plan 53B skid: 1.0 x 1.0 x 2.5m (500kg) Weights estimated based on Trillium reference.
O | S36 | 70 | UN | 36 | 0001 |  | 70-UN-36-0001 | HP Flare Metering Package | 2 | 2 | 0 |  | INS | Metering Package | 1 x 100% | Continuous |  |  | 0 - 681 | 0 - 561830 |  | 0.1 | 6 | -100 | 150 | FV | 15 | -115 | 165 |  |  | No | 3 | 3 | 2.5 |  |  | AZ-AB1-70-SK02-401150 | 316L (VTA) | Package contains ultrasonic flowmeters with dedicated pressure & temperature transmitters. The flowmeter is required to provide range from 0 to rated capacity specified. Requires straight pipe lengths of 15D upstream and 5D downstream. Rated flowrate represents maximum relieving case which will be intermittent.
O | S36 | 70 | UN | 36 | 0002 |  | 70-UN-36-0002 | LP Flare Metering Package | 2 | 2 | 0 |  | INS | Metering Package | 1 x 100% | Continuous |  |  | 0 - 23.2 | 0 - 19839 |  | 0.01 | 0.1 | -12 | 114 | FV | 9 | -46 | 130 |  |  | No | 2.5 | 2.5 | 2.5 |  |  | AZ-AB1-70-SK02-401152 | VTA | Package contains ultrasonic flowmeters with dedicated pressure & temperature transmitters. The flowmeter is required to provided capacity from 0 to rated capacity. Requires straight pipe lengths of 15D upstream and 5D downstream. Rated flowrate represents maximum relieving case which will be intermittent.
O | S36 | 70 | UZ | 36 | 0002 |  | 70-UZ-36-0002 | HP Flare Ignition Package | 2 | 2 | 0 |  | ME | Flare Package | 1 x 100% | Intermittent | [5 empty] | 0.1 | 6 | 20 | 20 | FV | 15 | -46 | 60 |  |  | Yes | 2.2 | 1.8 |  | 1000 |  | AZ-AB1-70-SK02-401150 | VTA | Flare stack to be normally purged with nitrogen, with fuel gas provided as automatic back-up. Flare tip to be ignited on loss of nitrogen. Package contains an on-demand pellet system for flare ignition, with a flame front generator supplied by fuel gas as back-up, and propane bottles supplied by vendor as an independent back-up to fuel gas. Air supply for pellet launch shall be provided with back-up supply by vendor which automatically activates in case of loss of primary air supply.
O | S36 | 70 | UZ | 36 | 0003 |  | 70-UZ-36-0003 | HP Flare Gas Recovery Package | 2 | 2 | 0 |  | ME | Flare Gas Recovery Package | 1 x 100% | Continuous |  |  | 1 |  |  | 0.1 | 8.80 | 35 | 45 | FV | 15 | -46 | 60 | 308.3 | 400 | No | 13.8 | 10.3 | 7.6 |  |  | AZ-AB1-70-SK02-401150 | Case: 316L Impellers: 316L | Flare Gas Recovery Unit (FRGU) supplied as a single packaged unit comprising 2x100% motor-driven API 681 Liquid Ring compressors, scrubbers, discharge (air) coolers, liquids recovery pump and associated local controls. Dimensions based on Garo's budgetary bid. Overall dimension can be split into: Compressor skid: 3.6 x 2.4 m (for each compressor) Air Cooler skid: 10.0 x 2.5 m (not including 1.5 x 1.5 access ladder along length) (approximate) Scrubber skid: 6.3 x 3.1m (approximate) Option 316L if minimum metal temperatures in any part of the system are less than that allowed for LTCS (-46°C). Soft Starter required for the motor as per Electrical Starting Study.
O | S36 | 70 | UZ | 36 | 0005 |  | 70-UZ-36-0005 | LP Flare Ignition Package | 2 | 2 | 0 |  | ME | Flare Package | 1 x 100% | Intermittent | [5 empty] | 0.01 | 0.1 | 20 | 20 | FV | 9 | -46 | 60 |  |  | Yes | 2.2 | 1.8 |  | 1000 |  | AZ-AB1-70-SK02-401152 | VTA | Flare stack to be normally purged with nitrogen, with fuel gas provided as automatic back-up. Flare tip to be ignited on loss of nitrogen. Package contains an on-demand pellet system for flare ignition, with a flame front generator supplied by fuel gas as back-up, and propane bottles supplied by vendor as an independent back-up to fuel gas. Air supply for pellet launch shall be provided with back-up supply by vendor which automatically activates in case of loss of primary air supply.
O | S36 | 70 | UZ | 36 | 0006 |  | 70-UZ-36-0006 | LP Flare Gas Recovery Package | 2 | 2 | 0 |  | ME | Flare Gas Recovery Package | 1 x 100% | Continuous |  |  | 1 |  |  | 0.01 | 8.80 | 35 | 45 | FV | 15 | -46 | 60 | 323 | 400 | No | 13.8 | 10.3 | 7.6 |  |  | AZ-AB1-70-SK02-401152 | Case: LTCS Impellers: 316L | Flare Gas Recovery Unit (FRGU) supplied as a single packaged unit comprising 2x100% motor-driven API 681 Liquid Ring compressors, scrubbers, discharge (air) coolers, liquids recovery pump and associated local controls. Dimensions based on Garo's budgetary bid. Overall dimension can be split into: Compressor skid: 3.6 x 2.4 m (for each compressor) Air Cooler skid: 10.0 x 2.5 m (not including 1.5 x 1.5 access ladder along length) (approximate) Scrubber skid: 6.3 x 3.1m (approximate) Soft Starter required for the motor as per Electrical Starting Study.
O | S36 | 70 | VZ | 36 | 0001 | A | 70-VZ-36-0001A | HP Flare KO Drum A | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 50% | Continuous |  |  |  | Vap: 350280 Liq: 199150 |  | 0.1 | 6 | -100 | 150 | FV | 15 | -115 | 165 | N/A | N/A | No | 16 | 4.4 |  | 81000 | 235000 | AZ-AB1-70-SK02-401150 | 316/316L SS | Horizontal two-phase separator in 2X50% configuration with both drums running in parallel. Two stab-in heaters, one on either end of drum, to be added. HP Flare KO Drums sized to receive 60 % of total vapour flow and 50 % of total liquid flow each.
O | S36 | 70 | VZ | 36 | 0001 | B | 70-VZ-36-0001B | HP Flare KO Drum B | 2 | 2 | 0 |  | ME | Pressure Vessel | 2 x 50% | Continuous |  |  |  | Vap: 350280 Liq: 199150 |  | 0.1 | 6 | -100 | 150 | FV | 15 | -115 | 165 | N/A | N/A | No | 16 | 4.4 |  | 81000 | 235000 | AZ-AB1-70-SK02-401150 | 316/316L SS | Horizontal two-phase separator in 2X50% configuration with both drums running in parallel. Two stab-in heaters, one on either end of drum, to be added. HP Flare KO Drums sized to receive 60 % of total vapour flow and 50 % of total liquid flow each.
O | S36 | 70 | VZ | 36 | 0002 |  | 70-VZ-36-0002 | LP Flare KO Drum | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  |  |  | Vap: 19884 Liq: 46607 |  | 0.01 | 0.1 | -12 | 114 | FV | 9 | -46 | 130 | N/A | N/A | No | 8 | 2.6 |  | 14000 |  | AZ-AB1-70-SK02-401152 | LTCS + Internal Lining | Horizontal separator with a single 1x100% electrical heater.
O | S43 | 70 | PA | 43 | 0001 | A | 70-PA-43-0001A | Rich MEG Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 17.0 |  |  |  | 0.1 | 8.3 | 23 | 37 | FV | 12 | -12 | 60 | 8.75 | 11 | No | 2.2 | 1.6 | 2.8 | 690 | 760 | AZ-AB1-70-SK02-401108 | Case: CS + 3.0mm CA Impeller: CS API 610 (S5) | Centrifugal 2X100% API 610 OH2 Dimensions and weight are based on Trillium budgetary bid, sizing based on Flowserve selection.
O | S43 | 70 | PA | 43 | 0001 | B | 70-PA-43-0001B | Rich MEG Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 17.0 |  |  |  | 0.1 | 8.3 | 23 | 37 | FV | 12 | -12 | 60 | 8.75 | 11 | No | 2.2 | 1.6 | 2.8 | 690 | 760 | AZ-AB1-70-SK02-401108 | Case: CS + 3.0mm CA Impeller: CS API 610 (S5) | Centrifugal 2X100% API 610 OH2 Dimensions and weight are based on Trillium budgetary bid, sizing based on Flowserve selection.
O | S43 | 70 | PA | 43 | 0003 | A | 70-PA-43-0003A | Lean MEG Transfer Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 6.0 |  |  |  | 0.3 | 5.1 | 50 | 50 | FV | 7 | -12 | 65 | 2.5 | 7.5 | No | 1.9 | 0.8 | 0.8 | 400 | 440 | AZ-AB1-70-SK02-401108 | Case: CS + 3.0mm CA Impeller: CS API 610 (S5) | Centrifugal 2X100% API 610 OH2 Dimensions and weight are based on Trillium budgetary bid, sizing based on Flowserve selection.
O | S43 | 70 | PA | 43 | 0003 | B | 70-PA-43-0003B | Lean MEG Transfer Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 6.0 |  |  |  | 0.3 | 5.1 | 50 | 50 | FV | 7 | -12 | 65 | 2.5 | 7.5 | No | 1.9 | 0.8 | 0.8 | 400 | 440 | AZ-AB1-70-SK02-401108 | Case: CS + 3.0mm CA Impeller: CS API 610 (S5) | Centrifugal 2X100% API 610 OH2 Dimensions and weight are based on Trillium budgetary bid, sizing based on Flowserve selection.
O | S43 | 70 | PA | 43 | 0004 |  | 70-PA-43-0004 | MEG Offloading Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 1 x 100% | Intermittent |  | 25 |  |  |  | 0.0 | 2.0 | AMB | 50 | FV | 6 | -12 | 60 | 3.63 | 7.5 | No | 2.2 | 1.6 | 2.8 | 710 | 780 | AZ-AB1-70-SK02-401108 | Case: CS + 3.0mm CA Impeller: CS API 610 (S5) | Centrifugal - intermittent use 1X100% API 610 OH2 Dimensions and weight are based on Trillium budgetary bid, sizing based on Flowserve selection.
O | S43 | 70 | TR | 43 | 0001 |  | 70-TR-43-0001 | Rich MEG Storage Tank | 2 | 2 | 0 |  | ME | Storage Tank | 1 x 100% | Continuous |  |  |  |  | 2434 | 0.3 | 0.4 | AMB | 40 | -0.0025 | 1.0 | -12 | 60 | N/A | N/A | No |  | 15 | 16.3 | 61000 | 2912000 | AZ-AB1-70-SK02-401108 | CS + 1.5mm CA + Internal Lining | API-620 Cone Roof (or equivalent) Tank Fuel Gas Blanketed Internal lining per AZ-AB1-70-SK02-140009 Rich MEG storage tank operated at low level to support 6 days of regeneration package outage (regeneration column out of service but MEG flash drum remains in service).
O | S43 | 70 | TR | 43 | 0002 |  | 70-TR-43-0002 | Lean MEG Storage Tank | 2 | 2 | 0 |  | ME | Storage Tank | 1 x 100% | Continuous |  |  |  |  | 1830 | 0.3 | 0.4 | AMB | 40 | -0.0025 | 1.0 | -12 | 65 | N/A | N/A | No |  | 15 | 12.8 | 51000 | 2294000 | AZ-AB1-70-SK02-401108 | CS + 1.5mm CA | API-620 Cone Roof (or equivalent) Tank Fuel Gas Blanketed Internal lining per AZ-AB1-70-SK02-140009 Lean MEG storage tank operated at high level to support subsea operations for up to 6 days of regeneration package outage.
O | S11 | 70 | UZ | 43 | 0001 |  | 70-UZ-43-0001 | Subsea MEG Injection Package | 2 | 2 | 0 |  | ME | Chemical Injection Package | 1 x 100% | Continuous |  | 9.5 |  |  |  |  | 505 | AMB | 43 | ATM | 690 | -12 | 60 | 148 | 185 | No | 10 | 2.4 | 2 | 1200 | 1320 | AZ-AB1-70-SK02-401108 | Materials for pumps and piping to be based on, CS + 3mm CA VTC | Package vendor to confirm requirement for separate pumps to support high pressure (normal operation) and very high pressure (infrequent) subsea operations. Pumps within package are of 2x100% arrangement. Dimensions and weight based on Veolia budgetary bid. Pumps to deliver 4.3m3/h normally (to be confirmed by Pipeline Contractor) and up to 9.5 m3/h periodically for up to 20 minutes. Package to include 2x100% Filters to achieve SAE AS4059 class 8 particle size specification.
O | S43 | 70 | UZ | 43 | 0002 |  | 70-UZ-43-0002 | MEG Regeneration Package | 2 | 2 | 0 |  | ME | Package | 1 x 100% | Continuous |  | 17 (Rich MEG) | [12 empty] | 3100 kW see column 18 | No | 35 [See notes] | 20 [See notes] | 20 [See notes] | 460000 | 525000 | AZ-AB1-70-SK02-401107 | VTA | Depending on Vendor, the package comprises of multiple skids for reassembly and interconnection at site as follows: 1. MEG flash drum skid 2. Rich MEG filtration skid 3. MEG regeneration package (incl. Electric reboilers). 4. Regenerator column. 5. Air coolers /condensers 6. Circulation Pumps Motors Electrical power consumption (based on Vendor Veolia's budgetary bid): Electric Heater: 3000 kW MEG Pump: 5.5 kW per pump (continuous) Reflux Pump: 15 kW per pump (continuous) MEG Cooler/Condenser: 50 (continuous) HC Drain pump: 4 kW per pump (intermittent) Note: Reflux pump discharge to be sufficient for 26 barg @ package boundary. Dimensions and weight are based on SLB budgetary bid.
O | S43 | 70 | HE | 70 | 0001 | A | 70-HE-70-0001A | Fuel Gas Heater | 2 | 2 | 0 |  | ME | Electrical Heater | 2 x 100% | Continuous | 40 | [5 empty] | 10 | -38 | 20 | FV | 17 | -75 | 60 | 40 | 48 | No | 1.5 | 0.2 |  | 450 |  | AZ-AB1-70-SK02-401158 | Shell: 316/316L SS Sheath (of element): 316 | Electric Heater, design inclusive of backup flows Duty presented is for 1 x 100% exchanger, with a design margin of 20% on duty (according to GS EP ECP 103). Dimensions and weight estimated based on DFINITI budgetary bid. Rated Power includes 20% margin on duty.
O | S43 | 70 | HE | 70 | 0001 | B | 70-HE-70-0001B | Fuel Gas Heater | 2 | 2 | 0 |  | ME | Electrical Heater | 2 x 100% | Continuous | 40 | [5 empty] | 10 | -38 | 20 | FV | 17 | -75 | 60 | 40 | 48 | No | 1.5 | 0.2 |  | 450 |  | AZ-AB1-70-SK02-401158 | Shell: 316/316L SS Sheath (of element): 316 | Electric Heater, design inclusive of backup flows Duty presented is for 1 x 100% exchanger, with a design margin of 20% on duty (according to GS EP ECP 103). Dimensions and weight estimated based on DFINITI budgetary bid. Rated Power includes 20% margin on duty.
O | S43 | 70 | VZ | 70 | 0001 |  | 70-VZ-70-0001 | Fuel Gas KO Drum | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  | 483 (Design) |  | 4070 (Design) | 0.39 (Working) | 10 | 10 | 20 | 20 | FV | 17 | -46 | 60 | N/A | N/A | No |  | 0.75 | 2.35 | 600 |  | AZ-AB1-70-SK02-401158 | LTCS | Vertical Vessel with demister. Sizing based on continuous fuel gas requirement from Utility Load List, with a 20% design margin Total working volume (to HHLL) = 0.39 m3 Total vessel volume = 1.15 m3 Sizing based on process data. Weight based on PVElite calculations.
O | S01 | 70 | UZ | 71 | 0001 |  | 70-UZ-71-0001 | Diesel Storage, Transfer Pumps and Filtration Package | 2 | 2 | 0 |  | ME | Package | 1 x 100% | Intermittent |  | 5 |  |  | 7 m^{3} (min storage working capacity) | ATM | 3 |  | AMB |  | 5 | -12 | 60 |  | 2x 2.2kW (duty/stand by) | No | 5 [See notes] | 4 [See notes] | 2.5 [See notes] | 2000 (estimate) | 10000 (estimate) | AZ-AB1-70-SK02-401162 | Casing: CS Internals: 316 | Diesel Storage, Transfer Pumps and Filtration Package is expected to comprise the following equipment: diesel storage, 2x100% diesel transfer pumps, 2x100% diesel filters and 2x100% diesel coalescers for particulates and water removal Diesel Storage tank (Capacity 9 m3 selected) is also part of vendor scope. Dimension and Weight provided are estimated value for the overall vendor scope.
O | S72 | 70 | EA | 72 | 0001 |  | 70-EA-72-0001 | Heating Medium Dump Cooler | 2 | 2 | 0 |  | ME | Air Cooler | 1 x 100% | Intermittent | 11372 | 135.1 | 34.2 | 129536 | 2.62 | 8.0 | 17.0 | 65 (Process Outlet) -12 (Air side Inlet) | 150 (Process Inlet) | FV | 20 | -12 | 165 | 46.3 (see remarks) | 3x 30kW (see remarks) | No | 12 | 6 | 4.4 | 44244 | 46861 | AZ-AB1-70-SK02-401159 | Header: CS + 3mm CA Tubes: 316 | Air Cooler 1X100%. Forced draft air cooler. 3x33% fans per bay @ Max Duty case / 3x50% fans per bay @ Min Duty case. Shipped to site as semi-assembled module with short legs. 1 bay, 2 bundles. Heat Transfer Area 9882.4 m2. 240 tubes per bundle / 25.4mm OD / 12.5m L / Extruded fins. No winterisation required.
O | S72 | 70 | PA | 72 | 0001 | A | 70-PA-72-0001A | Heating Medium Circulation Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 232.5 |  |  |  | 6.12 | 15.28 | 65 |  | FV | 17 | -12 | 165 | 79.2 | 90 | No | 2.8 | 1.8 | 2.8 | 1900 | 2090 | AZ-AB1-70-SK02-401159 | Casing: CS Impeller: 12% Cr API 610 (S6) | Centrifugal 2X100% API 610 OH2 Dimensions and weight are based on Trillium budgetary bid, sizing based on Flowserve selection.
O | S72 | 70 | PA | 72 | 0001 | B | 70-PA-72-0001B | Heating Medium Circulation Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 232.5 |  |  |  | 6.12 | 15.28 | 65 |  | FV | 17 | -12 | 165 | 79.2 | 90 | No | 2.8 | 1.8 | 2.8 | 1900 | 2090 | AZ-AB1-70-SK02-401159 | Casing: CS Impeller: 12% Cr API 610 (S6) | Centrifugal 2X100% API 610 OH2 Dimensions and weight are based on Trillium budgetary bid, sizing based on Flowserve selection.
O | S72 | 70 | UZ | 72 | 0001 | A | 70-UZ-72-0001A | Fired Heater Package A | 2 | 2 | 0 |  | ME | Fired Heater | 2 x 50% | Continuous | 10601 | [5 empty] | 15.0 | 65 | 150 |  | 20 | -12 | 165 |  | 10 | No | 6.3 | 3.7 | 10.7 | 33000 |  | AZ-AB1-70-SK02-401159 | Casing: CS+3mm CA Tubes: 316L (VTA) | Fired Heater 1 x 50% Each fired heater package shall comprise of the following equipment: heater, forced draft air system and burner management system. Rated duty includes 10% equipment duty margin. Dimensions based on Exotherm budgetary bid. Tube material: 316L as a minimum. 310 SS as an option.
O | S72 | 70 | UZ | 72 | 0001 | B | 70-UZ-72-0001B | Fired Heater Package B | 2 | 2 | 0 |  | ME | Fired Heater | 2 x 50% | Continuous | 10601 | [5 empty] | 15.0 | 65 | 150 |  | 20 | -12 | 165 |  | 10 | No | 6.3 | 3.7 | 10.7 | 33000 |  | AZ-AB1-70-SK02-401159 | Casing: CS+3mm CA Tubes: 316L (VTA) | Fired Heater 1 x 50% Each fired heater package shall comprise of the following equipment: heater, forced draft air system and burner management system. Rated duty includes 10% equipment duty margin. Dimensions based on Exotherm budgetary bid. Tube material: 316L as a minimum. 310 SS as an option.
O | S72 | 70 | VF | 72 | 0001 |  | 70-VF-72-0001 | Heating Medium Filter | 2 | 2 | 0 |  | ME | Filter Unit | 1 x 100% | Continuous | [6 empty] | 15.2 | 65 |  | FV | 20 | -12 | 165 | N/A | N/A | No | 2 | 0.6 | 2.1 (approx.) | 1000 | 1200 | AZ-AB1-70-SK02-401159 | Shell: CS + 3mm CA Internals: 316 | 1 x 100% Side stream flow (~10% of circulation) to heating medium filter to remove accumulated solids. Dimensions based on budgetary bid from ASCO FILTI.
O | S72 | 70 | VZ | 72 | 0001 |  | 70-VZ-72-0001 | Heating Medium Expansion Drum | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous | [6 empty] | 6.0 | 65 |  | FV | 15 | -12 | 165 | N/A | N/A | No | 5.2 | 2.6 |  | 13000 | 43000 | AZ-AB1-70-SK02-401159 | Shell: CS + 3mm CA | Horizontal 2 phase separator, to provide 12m^{3} working volume for expansion (LAL to LAH). Weight is based on PV Calc ; using FEED Process data
O | S72 | 70 | UB | 74 | 0001 |  | 70-UB-74-0001 | Nitrogen Generation Package | 2 | 2 | 0 |  | ME | Inert Gas Generator | [See notes] | Continuous |  | 620 Sm^{3} /h (Outlet) |  |  |  |  | 8.5 |  | AMB |  | 14 | -12 | 60 | 1 | 1 | No | 4.1 | 2.8 | 3.5 | 8000 | 8500 | AZ-AB1-70-SK02-401157 | VTA | Two trains: 2x100% (1 + 1 for sparing) on common skid Purity – 97 mol% N2 Type – membrane Inlet conditions – 8.5 barg Outlet Flow – 620 Sm3/h Inlet flow – estimated 1860 Sm3/h. Estimated 3:1 air to nitrogen ratio. Outlet conditions – 7.5 barg Max pressure drop across package – 1 bar Operating temperature – ATM Dew point – Air is dew pointed upstream via Air Dryer Package. GS dew point requirement of 20degC below min ambient of -12degC. Dimensions and weight based on Avesta budgetary bid.
O | S72 | 70 | VA | 74 | 0001 |  | 70-VA-74-0001 | Nitrogen Receiver | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  | 620 Sm^{3} /h (Outlet) |  |  |  | 6 | 8.5 |  | AMB | FV | 14 | -12 | 60 | N/A | N/A | No |  | 2.1 | 5 | 21879 |  | AZ-AB1-70-SK02-401157 | CS + 3mm CA | Sized for 15 minutes holdup
O | S43 | 70 | TZ | 75 | 0005 |  | 70-TZ-75-0005 | MEG Storage Day Tank | 2 | 2 | 0 | 70-UI-75-0001 | ME | Storage Tank | 1 x 100% | Continuous |  |  |  |  | 56 | 0.06 | 0.12 | Amb | 40 | -0.0025 | 0.17 + FULL OF LIQUID | -12 | 60 | N/A | N/A | No |  | 4 | 5.5 | 7000 | 254000 | AZ-AB1-70-SK02-401108 | CS +1.5mm CA | Included in 70-UZ-75-0001 supplier scope Internal lining per AZ-AB1-70-SK02-140009 MEG day tank provided for on-plot CPF users only.
O | S43 | 70 | UI | 75 | 0001 |  | 70-UI-75-0001 | Pour Point Depressant Injection Package | 2 | 2 | 0 |  | ME | Chemical Injection Package | 1 x 100% | Intermittent |  | 135 Litre/h |  |  | 23 m^{3} (min storage working capacity) |  | 51 |  | AMB |  | 526 | -12 | 60 | 0.21 | 0.75 | No | Skid: 3 Tank: 6.1 | Skid: 2.4 Tank: 2.5 | Skid: 2 Tank: 2.5 | Skid: 400 Tank: 4770 | Skid: 500 Tank: 29000 | AZ-AB1-70-SK02-401156 | 316L | API 675 Double Diaphragm Pump Package Chemical injection package located in containment bund. Each chemical injection package shall comprise of storage tank with a minimum of 14 days inventory, 2 x 100% dosing pumps. Package details to be finalised during detailed engineering. Dosing to cover 50% of the year when ambient is below 5 degC; based on coldest month January. Dimensions and weight based on Veolia budgetary bid - comprised of 1 x 20ft ISO tank and 1 x injection skid.
O | S43 | 70 | UI | 75 | 0002 |  | 70-UI-75-0002 | Corrosion Inhibitor Injection Package | 2 | 2 | 0 |  | ME | Chemical Injection Package | 1 x 100% | Continuous |  | 1 Litre/h |  |  | 1 m^{3} (min storage working capacity) |  | 4 |  | AMB |  | 6 | -12 | 60 | 0.00012 | 0.75 | No | 2.5 | 2.1 | 2.2 | 2500 | 4000 | AZ-AB1-70-SK02-401156 | 316L | API 675 Double Diaphragm Pump Package Chemical injection package located in containment bund. Each chemical injection package shall comprise of storage tank with a minimum of 14 days inventory, 2 x 100% dosing pumps. Package details to be finalised during detailed engineering. Dimensions and weight based on ICR budgetary bid - comprised of 1 x injection skid with tank installed on common base plate.
O | S43 | 70 | UI | 75 | 0003 |  | 70-UI-75-0003 | Biocide Injection Package | 2 | 2 | 0 |  | ME | Chemical Injection Package | 1 x 100% | Intermittent |  | 9 Litre/h |  |  | 1 m^{3} (min storage working capacity) |  | 0.5 |  | AMB |  | 3.5 | -12 | 60 | 0.00014 | 0.75 | No | 2.5 | 2.1 | 2.2 | 2500 | 4000 | AZ-AB1-70-SK02-401156 | 316L | API 675 Double Diaphragm Pump Package Chemical injection package located in containment bund. Each chemical injection package shall comprise of storage tank with a minimum of 14 days inventory, 2 x 100% dosing pumps. Package details to be finalised during detailed engineering. Batch dosing 4 hours, 3 times per week. Dimensions and weight based on ICR budgetary bid - comprised of 1 x injection skid with tank installed on common base plate
O | S43 | 70 | UI | 75 | 0004 |  | 70-UI-75-0004 | Oxygen Scavenger Injection Package | 2 | 2 | 0 |  | ME | Chemical Injection Package | 1 x 100% | Intermittent |  | 4 Litre/h |  |  | 1 m^{3} (min storage working capacity) |  | 9 |  | AMB |  | 17 | -12 | 60 | 0.00111 | 0.75 | No | 2.5 | 2.1 | 2.2 | 2500 | 4000 | AZ-AB1-70-SK02-401156 | 316L | API 675 Double Diaphragm Pump Package Chemical injection package located in containment bund. Each chemical injection package shall comprise of storage tank with a minimum of 14 days inventory, 2 x 100% dosing pumps. Package details to be finalised during detailed engineering. Batch dosing 4 hours, 3 times per week. Dimensions and weight based on ICR budgetary bid - comprised of 1 x injection skid with tank installed on common base plate
O | S43 | 70 | UZ | 75 | 0001 |  | 70-UZ-75-0001 | MEG Injection Package | 2 | 2 | 0 |  | ME | Chemical Injection Package | 1 x 100% | Continuous |  | 2.1 | [5 empty] | AMB | 43 | ATM | 526 (see remarks) | -12 | 60 | 3.56 | 7.5 | No | 4 | 2.4 | 2 | 800 | 880 | AZ-AB1-70-SK02-401108 | Materials for pumps and piping to be based on, CS + 3mm CA VTC | API 674 Triplex Plunger Pump Package Chemical injection package located in containment bund. Each chemical injection package shall comprise of storage tank with a minimum of 14 days inventory, 2 x 100% dosing pumps with dedicated heads for injecting into Slug Catcher gas outlet, Gas-Gas Exchanger and Turboexpander-Recompressor Suction Scrubber, and upstream of the choke valves. Package details to be finalised during detailed engineering. Injection skid dimensions and weight based on Veolia budgetary bid.
O | S01 | 70 | PA | 85 | 0001 | A | 70-PA-85-0001A | Utility Water Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 10 |  |  |  |  | 6 |  | AMB | 0 | 9 | -12 | 60 | 5.8 | 11 | No | 1.5 | 0.7 | 0.5 | 350 | 500 | AZ-AB1-70-SK02-401163 | API 610 (A-8) Casing: 316/316L Impeller:316/316L API 610 (A8) Option: Casing: Carbon Steel Impeller: 12% CR API 610 (S6) | ISO 5199 OH type Weights & Dimensions are based on Sulzer budgetary bid
O | S01 | 70 | PA | 85 | 0001 | B | 70-PA-85-0001B | Utility Water Pump | 2 | 2 | 0 |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 10 |  |  |  |  | 6 |  | AMB | 0 | 9 | -12 | 60 | 5.8 | 11 | No | 1.5 | 0.7 | 0.5 | 350 | 500 | AZ-AB1-70-SK02-401163 | API 610 (A-8) Casing: 316/316L Impeller:316/316L API 610 (A8) Option: Casing: Carbon Steel Impeller: 12% CR API 610 (S6) | ISO 5199 OH type Weights & Dimensions are based on Sulzer budgetary bid
O | S01 | 70 | TZ | 85 | 0001 |  | 70-TZ-85-0001 | Utility Water Storage Tank | 2 | 2 | 0 |  | ME | Storage Tank | 1 x 100% | Continuous |  |  |  |  | 92 m^{3} (working capacity) |  | ATM |  | AMB |  | ATM + FULL OF WATER | -12 | 60 | N/A | N/A | No |  | 5.3 | 5.8 | 9000 | 282000 | AZ-AB1-70-SK02-401163 | CS + 1.5mm CA All internal surfaces to be coated to Coating System T210
O | S01 | 70 | UU | 85 | 0001 |  | 70-UU-85-0001 | Utility Water Treatment Package | 2 | 2 | 0 |  | ME | Package | 1 x 100% | Continuous |  | 7.5 |  |  |  |  | 6 |  | AMB |  | 9 | -12 | 60 |  |  | No | 1.8 | 2.1 | 3.4 | 600 | 3900 | AZ-AB1-70-SK02-401163 | FILTERS: CS + 3mm CA + Internal Lining | Package is expected to comprise the following equipment: particulate filters, charcoal filters, UV sterilisers. Dimensions and weight based on Veolia budgetary bid. Alternative material selection 316L
O | S01 | 70 | PA | 01 | 0001 | A | 70-PA-01-0001A | Diesel Firewater Pump | 2 | 2 |  |  | ME | Centrifugal Pump | 4 x 33% | Intermittent |  | 990 |  |  |  | 0.5 | 14.5 | 0 | AMB | 12 | 16.8 | -12 | 60 |  | 522 | No | 8.5 | 3 | 4 | 17500 | 20000 | AZ-AB1-70-SK02-272086 | Casing: LTCS Impeller: 12% Cr API 610 (S6) | Diesel driven. Tested weekly (30 mins). Operating, design condition, dimensions and weights shall be obtained during FEED Emergency firewater supply to support the miscellaneous users. API 610 BB1. Miscellaneous Users: 15kW load Firewater Pump Packages (Diesel) are considered to comprise diesel-engine driven air-cooled horizontal centrifugal pumps, and associated ancillaries including local diesel day tank, air filtration, exhaust, lube oil and cooling systems, primary and secondary starting system, UCP and control system, fire and gas system with fire suppression system, complete within ventilated enclosure and lifting lugs for single point lift, etc. Dimensions and Weights are estimated using past project data and includes the enclosure, engine, day tank (2.5mx2mx2.25m, 1000 gallon) and auxiliaries required. Driver sizing and day tank dimensions and sizing are based on Ruhrpumpen budgetary bid.
O | S01 | 70 | PA | 01 | 0001 | B | 70-PA-01-0001B | Diesel Firewater Pump | 2 | 2 |  |  | ME | Centrifugal Pump | 4 x 33% | Intermittent |  | 990 |  |  |  | 0.5 | 14.5 | 0 | AMB | 12 | 16.8 | -12 | 60 |  | 522 | No | 8.5 | 3 | 4 | 17500 | 20000 | AZ-AB1-70-SK02-272086 | Casing: LTCS Impeller: 12% Cr API 610 (S6) | Diesel driven. Tested weekly (30 mins). Operating, design condition, dimensions and weights shall be obtained during FEED Emergency firewater supply to support the miscellaneous users. API 610 BB1. Miscellaneous Users: 15kW load Firewater Pump Packages (Diesel) are considered to comprise diesel-engine driven air-cooled horizontal centrifugal pumps, and associated ancillaries including local diesel day tank, air filtration, exhaust, lube oil and cooling systems, primary and secondary starting system, UCP and control system, fire and gas system with fire suppression system, complete within ventilated enclosure and lifting lugs for single point lift, etc. Dimensions and Weights are estimated using past project data and includes the enclosure, engine, day tank (2.5mx2mx2.25m, 1000 gallon) and auxiliaries required. Driver sizing and day tank dimensions and sizing are based on Ruhrpumpen budgetary bid.
O | S01 | 70 | PA | 01 | 0001 | C | 70-PA-01-0001C | Diesel Firewater Pump | 2 | 2 |  |  | ME | Centrifugal Pump | 4 x 33% | Intermittent |  | 990 |  |  |  | 0.5 | 14.5 | 0 | AMB | 12 | 16.8 | -12 | 60 |  | 522 | No | 8.5 | 3 | 4 | 17500 | 20000 | AZ-AB1-70-SK02-272086 | Casing: LTCS Impeller: 12% Cr API 610 (S6) | Diesel driven. Tested weekly (30 mins). Operating, design condition, dimensions and weights shall be obtained during FEED Emergency firewater supply to support the miscellaneous users. API 610 BB1. Miscellaneous Users: 15kW load Firewater Pump Packages (Diesel) are considered to comprise diesel-engine driven air-cooled horizontal centrifugal pumps, and associated ancillaries including local diesel day tank, air filtration, exhaust, lube oil and cooling systems, primary and secondary starting system, UCP and control system, fire and gas system with fire suppression system, complete within ventilated enclosure and lifting lugs for single point lift, etc. Dimensions and Weights are estimated using past project data and includes the enclosure, engine, day tank (2.5mx2mx2.25m, 1000 gallon) and auxiliaries required. Driver sizing and day tank dimensions and sizing are based on Ruhrpumpen budgetary bid.
O | S01 | 70 | PA | 01 | 0002 |  | 70-PA-01-0002 | Electric Firewater Pump | 2 | 2 |  |  | ME | Centrifugal Pump | 4 x 33% | Intermittent |  | 990 |  |  |  | 0.5 | 14.5 | 0 | AMB | 12 | 16.8 | -12 | 60 | 400.3 | 560 | Yes | 6.3 | 1.5 | 2.4 | 8000 | 9000 | AZ-AB1-70-SK02-272086 | Casing: LTCS Impeller: 12% Cr API 610 (S6) | Electric. Tested weekly (30 mins). API 610 BB1 Dimensions and weights are estimated using past projects and includes the enclosure and auxiliaries. Motor sizing based on Ruhrpumpen budgetary bid. Soft starter required for the motor as per Electrical Starting Study.
O | S01 | 70 | PA | 01 | 0003 | A | 70-PA-01-0003A | Firewater Jockey Pump | 2 | 2 |  |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 72 |  |  |  | 0.5 | 12.69 | 0 | AMB | 16 | 20 | -12 | 60 | 41.5 | 55 | No | 2 [See notes] | 0.7 [See notes] | 1.2 [See notes] | 650 | 750 | AZ-AB1-70-SK02-272086 | Casing: LTCS Impeller: 12% Cr API 610 (S6) | Electric. Jockeys are in 2x 100% configuration (duty/standby). API 610 OH1/2 Dimensions and weights are based on SPP budgetary bid data (bareshaft pump). Both firewater jockey pumps (70-PA-01-0003A/B) are required to be in a common weather proof enclosure. size of enclosure = 4.0m x 2.6m x 2.5m (empty weight 2300kg)
O | S01 | 70 | PA | 01 | 0003 | B | 70-PA-01-0003B | Firewater Jockey Pump | 2 | 2 |  |  | ME | Centrifugal Pump | 2 x 100% | Continuous |  | 72 |  |  |  | 0.5 | 12.69 | 0 | AMB | 16 | 20 | -12 | 60 | 41.5 | 55 | No | 2 [See notes] | 0.7 [See notes] | 1.2 [See notes] | 650 | 750 | AZ-AB1-70-SK02-272086 | Casing: LTCS Impeller: 12% Cr API 610 (S6) | Electric. Jockeys are in 2x 100% configuration (duty/standby). API 610 OH1/2 Dimensions and weights are based on SPP budgetary bid data (bareshaft pump). Both firewater jockey pumps (70-PA-01-0003A/B) are required to be in a common weather proof enclosure. size of enclosure = 4.0m x 2.6m x 2.5m (empty weight 2300kg)
O | S72 | 70 | PA | 01 | 0004 | A | 70-PA-01-0004A | Foam Pump Package | 2 | 2 |  |  | ME | Rotating Displacement Pumps | 2 x 100% | Intermittent |  | 79.2 |  |  |  | 0.5 | 16 | 0.0 | AMB | 16 | 17 | -15 | 52 | 78 | 90 | [See notes] | 3.5 [See notes] | 3 [See notes] | 2 [See notes] |  |  | AZ-AB1-70-SK02-272087 | Casing: 316L Impeller / Rotor: 316 | Single pump, part of common Foam pump skid below with 2x100% pumps overall. Pump/tanks, duties and capacities data TBD Emergency power supply to connect both foam pump skids, but consider one running during emergency event only. Electric-motor driven pumps @1500rpm together with common controller are mounted on a single skid 3.5m x 3m x 2m. Dimensions and weights estimated based on BB Con budgetary bid.
O | S72 | 70 | PA | 01 | 0004 | B | 70-PA-01-0004B | Foam Pump Package | 2 | 2 |  |  | ME | Rotating Displacement Pumps | 2 x 100% | Intermittent |  | 79.2 |  |  |  | 0.5 | 16 | 0.0 | AMB | 16 | 17 | -15 | 52 | 78 | 90 | [See notes] | 3.5 [See notes] | 3 [See notes] | 2 [See notes] |  |  | AZ-AB1-70-SK02-272087 | Casing: 316L Impeller / Rotor: 316 | Single pump, part of common Foam pump skid below with 2x100% pumps overall. Pump/tanks, duties and capacities data TBD Emergency power supply to connect both foam pump skids, but consider one running during emergency event only. Electric-motor driven pumps @1500rpm together with common controller are mounted on a single skid 3.5m x 3m x 2m. Dimensions and weights estimated based on BB Con budgetary bid.
O |  | 70 | SDE | 01 | 0001 |  | 70-SDE-01-0001 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 60 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 6 | 2.5 | 2.5 | 9500 | 11500 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 5 deluge valve configuration.
O |  | 70 | SDE | 01 | 0002 |  | 70-SDE-01-0002 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 72 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 6 | 2.5 | 2.5 | 9500 | 11500 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 5 deluge valve configuration.
O |  | 70 | SDE | 01 | 0003 |  | 70-SDE-01-0003 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 25 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 5 | 2.5 | 2.5 | 8000 | 9000 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 3 deluge valve configuration
O |  | 70 | SDE | 01 | 0004 |  | 70-SDE-01-0004 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 32 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 4 | 2.5 | 2.5 | 7000 | 8000 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 2 deluge valve configuration
O |  | 70 | SDE | 01 | 0005 |  | 70-SDE-01-0005 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 32 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 5 | 2.5 | 2.5 | 8000 | 9000 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 3 deluge valve configuration
O |  | 70 | SDE | 01 | 0006 |  | 70-SDE-01-0006 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 32 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 6 | 2.5 | 2.5 | 9500 | 11500 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 5 deluge valve configuration.
O |  | 70 | SDE | 01 | 0007 |  | 70-SDE-01-0007 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 32 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 6 | 2.5 | 2.5 | 9500 | 11500 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 5 deluge valve configuration.
O |  | 70 | SDE | 01 | 0008 |  | 70-SDE-01-0008 | Firewater Deluge Skid | 2 | 2 |  |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 32 |  |  | N/A | 8 | 10 | 0 | AMB | ATM | 16 | -10 | 52 | N/A | N/A | No | 4 | 2.5 | 2.5 | 7000 | 8000 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 2 deluge valve configuration
O |  | 70 | SDE | 01 | 0009 |  | 70-SDE-01-0009 | Firewater Deluge Skid | 2 | 2 | 0 |  | HSE | Deluge System | 1 x 100% | Intermittent |  | 32 |  |  | N/A |  |  |  |  | ATM | ATM | -10 | 52 | N/A | N/A | No | 4 | 2.5 | 2.5 | 7000 | 8000 | AZ-AB1-70-SK02-272087 | CS with SS 316 Trim deluge valve | Complete assembled skid, with associated firewater piping and instrumentation, supported on a structural steel frame and contained within a heated and insulated enclosure. 3% Foam Proportioned concentrate to be introduced in to the firewater supply down stream of the deluge valves. 2 deluge valve configuration
O | S01 | 70 | TZ | 01 | 0001 | A | 70-TZ-01-0001A | Firewater Storage Tank | 2 | 2 |  |  | ME | Storage Tank | 1 x 100% | Continuous |  |  |  |  | 7587 | ATM | ATM | [6 empty] | N/A | N/A | No |  | 26 | 15 | 180000 | 7956000 | AZ-AB1-70-SK02-272086 | CS + 1.5mm CA + Internal Lining | Cone-roof type, API 650, Net Working capacity = 7587 m3 Internal lining per AZ-AB1-70-SK02-140009
O | S01 | 70 | TZ | 01 | 0001 | B | 70-TZ-01-0001B | Firewater Storage Tank | 2 | 2 |  |  | ME | Storage Tank | 1 x 100% | Continuous |  |  |  |  | 7587 | ATM | ATM | [6 empty] | N/A | N/A | No |  | 26 | 15 | 180000 | 7956000 | AZ-AB1-70-SK02-272086 | CS + 1.5mm CA + Internal Lining | Cone-roof type, API 650, Net Working capacity = 7587 m3 Internal lining per AZ-AB1-70-SK02-140009
O | S72 | 70 | TZ | 01 | 0002 |  | 70-TZ-01-0002 | Firefighting Foam Storage Tank | 2 | 2 |  |  | ME | Storage Tank | 1 x 100% | Continuous |  |  |  |  | 50 |  |  | 32 | 50 | ATM | ATM | -10 | 52 | N/A | N/A | No |  | 5 | 3 | 7000 | 235000 | AZ-AB1-70-SK02-272087 | Shell, base and roof: 316L or CS +1.5mm CA + Internal Lining | Cone-roof type, API 650
O | S01 | 70 | DG | 05 | 0001 |  | 70-DG-05-0001 | Emergency Diesel Generator | 2 | 2 |  |  | ME | Diesel Generator | 1 x 100% | Intermittent | [7 empty] | -12 | 40 |  |  | -12 | 60 |  | 3 MVA | No | 12.5 | 3 | 4 | 18200 | 18900 |  |  | Preliminary estimate based on similar power rating. EMERGENCY GENERATOR UNIT is considered to comprised of diesel-engine driven air-cooled generator system, and associated ancillaries including 12 hrs local diesel day tank, air filtration, exhaust, lube oil and cooling systems, primary electric battery starting and secondary backup hydraulic starting system, UCP and control system, fire and gas system with fire suppression system, complete within ventilated enclosure and lifting lugs for single point lift , etc. ISO 8528 Diesel generator dimensions and weight estimated based on Cummins budgetary bid and MTU technical catalogue including enclosure and diesel tank.
O | S72 | 70 | UA | 07 | 0001 | A | 70-UA-07-0001A | Air Compressor Package | 2 | 2 | 0 |  | ME | Air Compressor | 3 x 50% | Continuous |  | 2250 Sm^{3} /h (Outlet, Dry basis) |  |  |  | 0 | 10.5 | AMB | 50 |  | 14 | -12 | 60 | 284 | 315 | Yes | 5.1 | 1.7 | 2.1 | 6210 |  | AZ-AB1-70-SK02-401157 | 316/316L | 3x50% Compressors ISO 10440-2 (Oil free Screw, 2-stage) Each air-cooled compressor package shall comprise of the following equipment: pulse jet inlet air filter, air compressor, interstage / discharge air coolers, moisture separators, and dust and oil filters. Dimensions and weight are based on Atlas Copco budgetary bid. Soft Starter required for the motor as per Electrical Starting Study.
O | S72 | 70 | UA | 07 | 0001 | B | 70-UA-07-0001B | Air Compressor Package | 2 | 2 | 0 |  | ME | Air Compressor | 3 x 50% | Continuous |  | 2250 Sm^{3} /h (Outlet, Dry basis) |  |  |  | 0 | 10.5 | AMB | 50 |  | 14 | -12 | 60 | 284 | 315 | No | 5.1 | 1.7 | 2.1 | 6210 |  | AZ-AB1-70-SK02-401157 | 316/316L | 3x50% Compressors ISO 10440-2 (Oil free Screw, 2-stage) Each air-cooled compressor package shall comprise of the following equipment: pulse jet inlet air filter, air compressor, interstage / discharge air coolers, moisture separators, and dust and oil filters. Dimensions and weight are based on Atlas Copco budgetary bid.
O | S72 | 70 | UA | 07 | 0001 | C | 70-UA-07-0001C | Air Compressor Package | 2 | 2 | 0 |  | ME | Air Compressor | 3 x 50% | Continuous |  | 2250 Sm^{3} /h (Outlet, Dry basis) |  |  |  | 0 | 10.5 | AMB | 50 |  | 14 | -12 | 60 | 284 | 315 | No | 5.1 | 1.7 | 2.1 | 6210 |  | AZ-AB1-70-SK02-401157 | 316/316L | 3x50% Compressors ISO 10440-2 (Oil free Screw, 2-stage) Each air-cooled compressor package shall comprise of the following equipment: pulse jet inlet air filter, air compressor, interstage / discharge air coolers, moisture separators, and dust and oil filters. Dimensions and weight are based on Atlas Copco budgetary bid.
O | S72 | 70 | UZ | 07 | 0001 | A | 70-UZ-07-0001A | Air Dryer Package | 2 | 2 | 0 |  | ME | Air Dryer Package | 2 x 100% | Continuous |  | 7650 Sm^{3} /h (Inlet) |  |  |  |  | 9.5 | AMB | 50 |  | 14 | -12 | 60 |  |  | No | 1.7 | 2.2 | 2.4 | 2300 | 2300 | AZ-AB1-70-SK02-401157 | 316/316L | Each air dryer package shall include at least desiccant beds, inlet and after filters. Dimensions are based on Ingersoll Rand budgetary bid. Flow is 1.7 times of total nominal flow of air compressors as per GS EP MEC 033 (4500 Sm3/h x 1.7)
O | S72 | 70 | UZ | 07 | 0001 | B | 70-UZ-07-0001B | Air Dryer Package | 2 | 2 | 0 |  | ME | Air Dryer Package | 2 x 100% | Continuous |  | 7650 Sm^{3} /h (Inlet) |  |  |  |  | 9.5 | AMB | 50 |  | 14 | -12 | 60 |  |  | No | 1.7 | 2.2 | 2.4 | 2300 | 2300 | AZ-AB1-70-SK02-401157 | 316/316L | Each air dryer package shall include at least desiccant beds, inlet and after filters. Dimensions are based on Ingersoll Rand budgetary bid. Flow is 1.7 times of total nominal flow of air compressors as per GS EP MEC 033 (4500 Sm3/h x 1.7)
O | S72 | 70 | VA | 07 | 0001 |  | 70-VA-07-0001 | Dry Air Receiver | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  | 3790 Sm3/h |  |  |  | 7 | 9.5 |  | AMB | FV | 14 | -12 | 60 | N/A | N/A | No |  | 3.9 | 10 | 28984 |  | AZ-AB1-70-SK02-401157 | CS + 3mm CA | Sized for 20 minutes holdup
O | S72 | 70 | VA | 07 | 0002 |  | 70-VA-07-0002 | Wet Air Receiver | 2 | 2 | 0 |  | ME | Pressure Vessel | 1 x 100% | Continuous |  | 4500 Sm^{3} /h |  |  |  | 8 | 10.5 |  | AMB | FV | 14 | -12 | 60 | N/A | N/A | No |  | 1.3 | 2.8 | 3348 |  | AZ-AB1-70-SK02-401157 | LTCS + 3mm CA + Internal Lining | Sized for 1 minutes holdup to allow for compressor change-over Internal Lining per AZ-AB1-70-SK02-140009
O | S80 | 70 | FCU | 09 | 0001 |  | 70-FCU-09-0001 | Fan Coil Unit for Paint Store | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 50% | Duty | 1.3 | 360 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.10 | 0.37 |  | 0.7 | 0.5 | 0.3 | 25 | 25
O | S80 | 70 | FCU | 09 | 0002 |  | 70-FCU-09-0002 | Fan Coil Unit for Paint Store | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 50% | Duty | 1.3 | 360 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.10 | 0.37 |  | 0.7 | 0.5 | 0.3 | 25 | 25
O | S80 | 70 | FCU | 09 | 0003 |  | 70-FCU-09-0003 | Fan Coil Unit for Telecom Room (Workshop building) | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 3.1 | 700 | [11 empty] | 0.10 | 0.37 |  | 0.9 | 0.3 | 0.23 | 28 | 28 |  |  | DX Type
O | S80 | 70 | FCU | 09 | 0004 |  | 70-FCU-09-0004 | Fan Coil Unit for Electrical Room (Workshop building) | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 7.8 | 1300 | [11 empty] | 0.18 | 0.37 |  | 1.1 | 0.35 | 0.25 | 40 | 40 |  |  | DX Type
O | S80 | 70 | FCU | 09 | 0005 |  | 70-FCU-09-0005 | Fan Coil Unit for Security Hut 01 | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 2.5 | 600 | [11 empty] | 0.10 | 0.37 |  | 0.6 | 0.6 | 0.25 | 20 | 20 | AZ-AB1-70-SK02-222009 |  | Cassette Type Split AC Dx Unit
O | S80 | 70 | FCU | 09 | 0006 |  | 70-FCU-09-0006 | Fan Coil Unit for Security Hut 02 | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 300 | [11 empty] | 0.10 | 0.37 |  | 0.6 | 0.6 | 0.25 | 20 | 20 | AZ-AB1-70-SK02-222009 |  | Cassette Type Split AC Dx Unit
O | S80 | 70 | FCU | 09 | 0007 |  | 70-FCU-09-0007 | Fan Coil Unit for Security Hut 02 | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 2.3 | 600 | [11 empty] | 0.10 | 0.37 |  | 0.6 | 0.6 | 0.25 | 20 | 20 | AZ-AB1-70-SK02-222009 |  | Cassette Type Split AC Dx Unit
O | S80 | 70 | FCU | 09 | 0008 |  | 70-FCU-09-0008 | Fan Coil Unit for Break Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 2.9 | 860 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0009 |  | 70-FCU-09-0009 | Fan Coil Unit for Meeting Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 2.4 | 720 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0010 |  | 70-FCU-09-0010 | Fan Coil Unit for Meeting Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 2.4 | 720 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0011 |  | 70-FCU-09-0011 | Fan Coil Unit for Reception, lobby and Waiting room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.5 | 450 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0012 |  | 70-FCU-09-0012 | Fan Coil Unit for Reception, lobby and Waiting room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.5 | 450 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0013 |  | 70-FCU-09-0013 | Fan Coil Unit for Male Toilet | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 0.3 | 90 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0014 |  | 70-FCU-09-0014 | Fan Coil Unit for Female Toilet | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 0.3 | 80 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0015 |  | 70-FCU-09-0015 | Fan Coil Unit for Medical Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 0.8 | 608 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0016 |  | 70-FCU-09-0016 | Fan Coil Unit for Meeting Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.9 | 570 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0017 |  | 70-FCU-09-0017 | Fan Coil Unit for Print room store | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 0.8 | 600 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0018 |  | 70-FCU-09-0018 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 5.5 | 1600 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 1.1 | 0.35 | 0.25 | 40 | 40
O | S80 | 70 | FCU | 09 | 0019 |  | 70-FCU-09-0019 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 5.5 | 1600 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 1.1 | 0.35 | 0.25 | 40 | 40
O | S80 | 70 | FCU | 09 | 0020 |  | 70-FCU-09-0020 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0021 |  | 70-FCU-09-0021 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0022 |  | 70-FCU-09-0022 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0023 |  | 70-FCU-09-0023 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0024 |  | 70-FCU-09-0024 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0025 |  | 70-FCU-09-0025 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0026 |  | 70-FCU-09-0026 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0027 |  | 70-FCU-09-0027 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0028 |  | 70-FCU-09-0028 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0029 |  | 70-FCU-09-0029 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0030 |  | 70-FCU-09-0030 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0031 |  | 70-FCU-09-0031 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 1.3 | 400 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 0.6 | 0.6 | 0.25 | 20 | 20
O | S80 | 70 | FCU | 09 | 0032 |  | 70-FCU-09-0032 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 5.5 | 1600 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 1.1 | 0.35 | 0.25 | 40 | 40
O | S80 | 70 | FCU | 09 | 0033 |  | 70-FCU-09-0033 | Fan Coil Unit for Office Room | 2 | 2 | 0 |  | HV | Fan Coil Unit | 1 x 100% | Continuous | 5.5 | 1600 | [5 empty] | -4 | 40 |  |  | -4 | 35 | 0.1 | 0.2 |  | 1.1 | 0.35 | 0.25 | 40 | 40
O | S80 | 70 | HE | 09 | 0001 |  | 70-HE-09-0001 | Duct Heater for Office (Warehouse building) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 2.10 | 800 | [11 empty] | 2.00 | 2.00 |  | 0.3 | 0.4 | 0.2 | 18 | 18 |  |  | Office
O | S80 | 70 | HE | 09 | 0002 |  | 70-HE-09-0002 | Duct Heater for Break Room (Warehouse building) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1.6 | 600 | [11 empty] | 1.50 | 1.50 |  | 0.3 | 0.3 | 0.2 | 14 | 14 |  |  | Break Room
O | S80 | 70 | HE | 09 | 0003 |  | 70-HE-09-0003 | Duct Heater for Office Room (Workshop building) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.8 | 180 | [11 empty] | 0.80 | 0.80 |  | 0.3 | 0.3 | 0.2 | 14 | 14
O | S80 | 70 | HE | 09 | 0004 |  | 70-HE-09-0004 | Duct Heater for Break/Dining Room (Workshop building) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1.7 | 180 | [11 empty] | 1.50 | 1.50 |  | 0.4 | 0.4 | 0.3 | 22 | 22
O | S80 | 70 | HE | 09 | 0005 |  | 70-HE-09-0005 | Duct Heater for Male Changing Room (Workshop building) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 710 | [11 empty] | 0.50 | 0.50 |  | 0.3 | 0.15 | 0.15 | 12 | 10
O | S80 | 70 | HE | 09 | 0006 |  | 70-HE-09-0006 | Duct Heater for Female Changing Room (Workshop building) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 425 | [11 empty] | 0.50 | 0.50 |  | 0.3 | 0.15 | 0.15 | 12 | 10 |  |  | Male Changing Room
O | S80 | 70 | HE | 09 | 0007 |  | 70-HE-09-0007 | Duct Heater for office (Fire Station) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 2.4 | 900 | [11 empty] | 2.4 | 2.4 |  | 0.3 | 0.3 | 0.2 | 14 | 14 |  |  | Female Changing Room
O | S80 | 70 | HE | 09 | 0008 |  | 70-HE-09-0008 | Duct Heater for Male Changing Room (Fire Station) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1.8 | 600 | [11 empty] | 1.8 | 1.8 |  | 0.3 | 0.3 | 0.15 | 12 | 12 |  |  | Security Office
O | S80 | 70 | HE | 09 | 0009 |  | 70-HE-09-0009 | Duct Heater for Female Changing Room (Fire Station) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1 | 325 | [11 empty] | 1 | 1 |  | 0.3 | 0.3 | 0.15 | 12 | 12 |  |  | Lobby (North)
O | S89 | 70 | HE | 09 | 0010 |  | 70-HE-09-0010 | Duct Heater for Security Office (Main gate House) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 7.9 | 3000 | [11 empty] | 7.9 | 7.9 |  | 0.5 | 0.7 | 0.3 | 40 | 40 |  |  | Lobby (South)
O | S89 | 70 | HE | 09 | 0011 |  | 70-HE-09-0011 | Duct Heater for Staff Break Room (Main Gate House) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 2.8 | 1100 | [11 empty] | 2.8 | 2.8 |  | 0.4 | 0.4 | 0.2 | 20 | 20 |  |  | Staff Break Room
O | S89 | 70 | HE | 09 | 0012 |  | 70-HE-09-0012 | Duct Heater for Staff Locker Room (Main Gate House) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.6 | 225 | [11 empty] | 0.6 | 0.6 |  | 0.3 | 0.15 | 0.15 | 10 | 10 |  |  | Telecom Room
O | S72 | 70 | HE | 09 | 0013 |  | 70-HE-09-0013 | Duct Heater for HVAC Room (East ITR) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Duty | 4.4 | 3282 | [11 empty] | 4.40 | 4.40 |  | 1 | 0.8 | 0.5 | 65 | 65
O | S72 | 70 | HE | 09 | 0014 |  | 70-HE-09-0014 | Duct Heater for Tech Room (East ITR) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Duty | 13.5 | 9849 | [11 empty] | 13.50 | 13.50 |  | 1 | 1 | 0.5 | 45 | 45
O | S43 | 70 | HE | 09 | 0015 |  | 70-HE-09-0015 | Duct Heater for HVAC Room (West ITR) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Duty | 4.6 | 3454 | [11 empty] | 4.40 | 4.40 |  | 1 | 0.8 | 0.5 | 35 | 35
O | S43 | 70 | HE | 09 | 0016 |  | 70-HE-09-0016 | Duct Heater for Tech Room (West ITR) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Duty | 13.5 | 9843 | [11 empty] | 13.50 | 13.50 |  | 1 | 1 | 0.5 | 85 | 85
O | S01 | 70 | HE | 09 | 0017 |  | 70-HE-09-0017 | Duct Heater for CTR (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1.7 | 5000 | [11 empty] | 1.70 | 1.70 |  | 0.7 | 0.7 | 0.5 | 45 | 45
O | S01 | 70 | HE | 09 | 0018 |  | 70-HE-09-0018 | Duct Heater for Corridor (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 750 | [11 empty] | 0.50 | 0.50 |  | 0.3 | 0.2 | 0.15 | 15 | 15
O | S01 | 70 | HE | 09 | 0019 |  | 70-HE-09-0019 | Duct Heater for CCR (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 6 | 15700 | [11 empty] | 6.00 | 6.00 |  | 1 | 1.3 | 0.5 | 110 | 110
O | S01 | 70 | HE | 09 | 0020 |  | 70-HE-09-0020 | Duct Heater for Engineering Room (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 700 | [11 empty] | 0.50 | 0.50 |  | 0.3 | 0.3 | 0.15 | 13 | 13
O | S01 | 70 | HE | 09 | 0021 |  | 70-HE-09-0021 | Duct Heater for Emergency Response Room (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1 | 810 | [11 empty] | 1.00 | 1.00 |  | 0.3 | 0.3 | 0.25 | 14 | 14
O | S01 | 70 | HE | 09 | 0022 |  | 70-HE-09-0022 | Duct Heater for OTS (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 550 | [11 empty] | 0.50 | 0.50 |  | 0.3 | 0.3 | 0.15 | 13 | 13
O | S01 | 70 | HE | 09 | 0023 |  | 70-HE-09-0023 | Duct Heater for Maintenance Room (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 750 | [11 empty] | 0.50 | 0.50 |  | 0.3 | 0.3 | 0.15 | 13 | 13
O | S01 | 70 | HE | 09 | 0024 |  | 70-HE-09-0024 | Duct Heater for Office (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1 | 1150 | [11 empty] | 1.00 | 1.00 |  | 0.7 | 0.3 | 0.3 | 15 | 15
O | S01 | 70 | HE | 09 | 0025 |  | 70-HE-09-0025 | Duct Heater for Entrance Waiting Room (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1 | 1000 | [11 empty] | 1.00 | 1.00 |  | 0.3 | 0.3 | 0.3 | 15 | 15
O | S01 | 70 | HE | 09 | 0026 |  | 70-HE-09-0026 | Duct Heater for Break Room (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1 | 900 | [11 empty] | 1.00 | 1.50 |  | 0.3 | 0.3 | 0.3 | 15 | 15
O | S01 | 70 | HE | 09 | 0027 |  | 70-HE-09-0027 | Duct Heater for Male Changing Room (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 150 | [11 empty] | 0.50 | 0.50 |  | 0.2 | 0.15 | 0.15 | 10 | 10
O | S01 | 70 | HE | 09 | 0028 |  | 70-HE-09-0028 | Duct Heater for Female Changing Room (Control Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 0.5 | 150 | [11 empty] | 0.50 | 0.50 |  | 0.2 | 0.15 | 0.15 | 10 | 10
O | S80 | 70 | HE | 09 | 0029 |  | 70-HE-09-0029 | Duct Heater for Telecom R (Admin Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 7.3 | 3000 | [11 empty] | 7.3 | 7.3 |  | 1 | 0.8 | 0.4 | 60 | 60
O | S80 | 70 | HE | 09 | 0030 |  | 70-HE-09-0030 | Duct Heater for Electrical R (Admin Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 1.7 | 1250 | [11 empty] | 1.7 | 1.7 |  | 0.7 | 0.4 | 0.3 | 20 | 20
O | S80 | 70 | HE | 09 | 0031 |  | 70-HE-09-0031 | Duct Heater for HVAC R (Admin Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 2.5 | 1850 | [11 empty] | 2.5 | 2.5 |  | 0.7 | 0.5 | 0.4 | 35 | 35
O | S80 | 70 | HE | 09 | 0032 |  | 70-HE-09-0032 | Duct Heater for Laboratory Room (Laboratory Bldg) | 2 | 2 | 0 |  | HV | Electrical Heater | 1 x 100% | Continuous | 9.4 | 1346 | [11 empty] | 9.4 | 9.4 |  | 0.5 | 0.5 | 0.3 | 10 | 10
O | S80 | 70 | KE | 09 | 0001 |  | 70-KE-09-0001 | Exhaust Fan for Paint Store (Warehouse building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 50% | Duty |  | 360 | [11 empty] | 0.02 | 0.37 |  | 0.2 | 0.15 | 0.15 | 12 | 12 |  |  | Fresh Air Fan for Paint Store
O | S80 | 70 | KE | 09 | 0002 |  | 70-KE-09-0002 | Exhaust Fan for Paint Store (Warehouse building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 50% | Duty |  | 360 | [11 empty] | 0.02 | 0.37 |  | 0.2 | 0.15 | 0.15 | 12 | 12 |  |  | Fresh Air Fan for Paint Store
O | S80 | 70 | KE | 09 | 0003 |  | 70-KE-09-0003 | Exhaust Fan for WC (Warehouse building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous |  | 61 | [11 empty] | 0.02 | 0.37 |  | 0.1 | 0.1 | 0.1 | 5 | 5 |  |  | W/C Extract Fan
O | S80 | 70 | KE | 09 | 0004 |  | 70-KE-09-0004 | Exhaust Fan for Toilets (Workshop building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous |  | 440 | [11 empty] | 0.08 | 0.37 |  | 0.3 | 0.3 | 0.25 | 10 | 10
O | S80 | 70 | KE | 09 | 0005 |  | 70-KE-09-0005 | Exhaust Fan for Mechanical Workshop (Workshop building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous |  | 13507 | [11 empty] | 2.50 | 4.00
O | S80 | 70 | KE | 09 | 0006 |  | 70-KE-09-0006 | Exhaust Fan for Welding Bay (Workshop building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous |  | 1500 | [11 empty] | 0.27 | 0.55
O | S80 | 70 | KE | 09 | 0007 |  | 70-KE-09-0007 | Exhaust Fan for Painting Bay (Workshop building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous |  | 1500 | [11 empty] | 0.27 | 0.55
O | S80 | 70 | KE | 09 | 0008 |  | 70-KE-09-0008 | Exhaust Fan for Changing Room (Fire Station) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.25 | 700 | [11 empty] | 0.13 | 0.37 |  | 0.35 | 0.35 | 0.3 | 14 | 14
O | S80 | 70 | KE | 09 | 0009 |  | 70-KE-09-0009 | Exhaust Fan for workshop (Fire Station) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.18 | 500 | [11 empty] | 0.09 | 0.37 |  | 0.3 | 0.3 | 0.25 | 10 | 10
O | S89 | 70 | KE | 09 | 0010 |  | 70-KE-09-0010 | Exhaust Fan for Staff Locker Room (Main Gate House) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.2 | 250 | [11 empty] | 0.10 | 0.37 |  | 0.2 | 0.15 | 0.15 | 5 | 5
O | S72 | 70 | KE | 09 | 0011 | A | 70-KE-09-0011A | Exhaust Fan for Battery Room (East ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 1.1 | 3000 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 40
O | S72 | 70 | KE | 09 | 0011 | B | 70-KE-09-0011B | Exhaust Fan for Battery Room (East ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 1.1 | 3000 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 40
O | S72 | 70 | KE | 09 | 0012 | A | 70-KE-09-0012A | Exhaust Fan for HVAC Room (East ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 1.1 | 3000 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 40
O | S72 | 70 | KE | 09 | 0012 | B | 70-KE-09-0012B | Exhaust Fan for HVAC Room (East ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 1.1 | 3000 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 40
O | S43 | 70 | KE | 09 | 0013 | A | 70-KE-09-0013A | Exhaust Fan for Battery Room (West ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 1.1 | 3200 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 45
O | S43 | 70 | KE | 09 | 0013 | B | 70-KE-09-0013B | Exhaust Fan for Battery Room (West ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 1.1 | 3200 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 45
O | S43 | 70 | KE | 09 | 0014 | A | 70-KE-09-0014A | Exhaust Fan for HVAC Room (West ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 1.1 | 3200 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 45
O | S43 | 70 | KE | 09 | 0014 | B | 70-KE-09-0014B | Exhaust Fan for HVAC Room (West ITR) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 1.1 | 3200 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 45
O | S01 | 70 | KE | 09 | 0015 | A | 70-KE-09-0015A | Exhaust Fan for Clean Agent Fire Suppression Room (Control Bldg)) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 0.18 | 500 | [11 empty] | 0.09 | 0.37 |  | 0.3 | 0.3 | 0.25 | 10 | 10
O | S01 | 70 | KE | 09 | 0015 | B | 70-KE-09-0015B | Exhaust Fan for Clean Agent Fire Suppression Room (Control Bldg)) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 0.18 | 500 | [11 empty] | 0.09 | 0.37 |  | 0.3 | 0.3 | 0.25 | 10 | 10
O | S01 | 70 | KE | 09 | 0016 | A | 70-KE-09-0016A | Exhaust Fan for Battery Room (Control Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 1.1 | 3000 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 40
O | S01 | 70 | KE | 09 | 0016 | B | 70-KE-09-0016B | Exhaust Fan for Battery Room (Control Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 1.1 | 3000 | [11 empty] | 0.75 | 1.10 |  | 800 | 600 | 600 | 80 | 40
O | S80 | 70 | KE | 09 | 0017 |  | 70-KE-09-0017 | Exhaust Fan for Janitor, Toilets, Showers (Control Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.15 | 400 | [11 empty] | 0.10 | 0.37 |  | 0.2 | 0.15 | 0.15 | 5 | 5
O | S80 | 70 | KE | 09 | 0018 | A | 70-KE-09-0018A | Exhaust Fan for Battery Room (Admin Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 0.25 | 500 | [11 empty] | 0.18 | 0.37 |  | 0.6 | 0.3 | 0.2 | 25 | 25
O | S80 | 70 | KE | 09 | 0018 | B | 70-KE-09-0018B | Exhaust Fan for Battery Room (Admin Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 0.25 | 500 | [11 empty] | 0.18 | 0.37 |  | 0.6 | 0.3 | 0.2 | 25 | 25
O | S80 | 70 | KE | 09 | 0019 | A | 70-KE-09-0019A | Exhaust Fan for HVAC Room (Admin Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Duty | 0.75 | 1850 | [11 empty] | 0.55 | 0.75 |  | 0.8 | 0.4 | 0.3 | 45 | 45
O | S80 | 70 | KE | 09 | 0019 | B | 70-KE-09-0019B | Exhaust Fan for HVAC Room (Admin Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Standby | 0.75 | 1850 | [11 empty] | 0.55 | 0.75 |  | 0.8 | 0.4 | 0.3 | 45 | 45
O | S80 | 70 | KE | 09 | 0020 |  | 70-KE-09-0020 | Exhaust Fan for WC (Admin Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.37 | 820 | [11 empty] | 0.25 | 0.37 |  | 0.5 | 0.3 | 0.2 | 28 | 28
O | S80 | 70 | KE | 09 | 0021 |  | 70-KE-09-0021 | Exhaust Fan for Medical R (Admin Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.18 | 300 | [11 empty] | 0.10 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S80 | 70 | KE | 09 | 0022 |  | 70-KE-09-0022 | Exhaust Room for Break R (Admin Bldg) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.18 | 300 | [11 empty] | 0.10 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S89 | 70 | KE | 09 | 0025 | A | 70-KE-09-0025A | Exhaust Room for HVAC Room (Main Gate House) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Continuous | 0.15 | 400 | [11 empty] | 0.20 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S89 | 70 | KE | 09 | 0025 | B | 70-KE-09-0025B | Exhaust Room for HVAC Room (Main Gate House) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Continuous | 0.15 | 400 | [11 empty] | 0.20 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S89 | 70 | KE | 09 | 0026 |  | 70-KE-09-0026 | Exhaust Fan for Laboratory (Laboratory Building) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Continuous | 0.2 | 1288 | [11 empty] | 0.20 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S89 | 70 | KE | 09 | 0027 |  | 70-KE-09-0027 | Exhaust Fan for HVAC Room (Laboratory Building) | 2 | 2 | 0 |  | HV | Fan Package | 2 x 100% | Continuous | 0.15 | 600 | [11 empty] | 0.20 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S89 | 70 | KE | 09 | 0028 |  | 70-KE-09-0028 | Exhaust Fan for Technical Rooms (Laboratory Building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.15 | 600 | [11 empty] | 0.20 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S89 | 70 | KE | 09 | 0029 |  | 70-KE-09-0029 | Exhaust Fan for Toilet (Laboratory Building) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.1 | 40 | [11 empty] | 0.10 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S80 | 70 | KE | 09 | 0030 |  | 70-KE-09-0030 | Exhaust Room for WC (Security Hut 02) | 2 | 2 | 0 |  | HV | Fan Package | 1 x 100% | Continuous | 0.1 | 40 | [11 empty] | 0.10 | 0.37 |  | 0.4 | 0.2 | 0.15 | 18 | 18
O | S80 | 70 | QA | 09 | 0001 |  | 70-QA-09-0001 | Supply Air Handling Unit (Warehouse building) | 2 | 2 | 0 |  | HV | Air Handling Unit | 1 x 100% | Continuous | 96.3 | 18119 |  | 21743 |  |  |  | -4 | 40 |  |  | -4 | 35 | 0.57 | 1.10 |  | 4.2 | 1.8 | 2.2 | 950 | 1100 | AZ-AB1-70-SK02-222004 | SS316L | incl. outdoor air flow 1213 m3/h
O | S80 | 70 | QA | 09 | 0002 |  | 70-QA-09-0002 | Supply Air Handling Unit for Workshop Building | 2 | 2 | 0 |  | HV | Air Handling Unit | 1 x 100% | Continuous | 509.5 | 23807 |  | 28568 |  |  |  | -4 | 40 |  |  | -4 | 35 | 9.00 | 15.00 |  | 4.2 | 1.8 | 2.2 | 950 | 1100 | AZ-AB1-70-SK02-220003 | SS316L | 100% fresh air
O | S80 | 70 | QA | 09 | 0003 |  | 70-QA-09-0003 | DX type Air Handling Unit (Fire Station) | 2 | 2 | 0 |  | HV | Air Handling Unit | 1 x 100% | Continuous | 73.3 | 5850 |  | 7020 | [7 empty] | -4 | 35 | 1.20 | 1.50 |  | 2.8 | 1 | 1.5 | 750 | 800 | AZ-AB1-70-SK02-222005 | SS316L
O | S89 | 70 | QA | 09 | 0004 |  | 70-QA-09-0004 | DX type Air Handling Unit (Main Gate House) | 2 | 2 | 0 |  | HV | Air Handling Unit | 1 x 100% | Continuous | 47.2 | 6624 |  | 7949 | [7 empty] | -4 | 35 | 2.20 | 4.00 |  | 2.6 | 1.2 | 1.5 | 450 | 500 | AZ-AB1-70-SK02-222008 | SS316L
O | S72 | 70 | QA | 09 | 0005 | A | 70-QA-09-0005A | Air Handling Unit for East ITR | 2 | 2 | 0 |  | HV | Air Handling Unit | 2 x 100% | Duty | 214.4 | 16700 |  | 20040 |  |  |  | -4 | 40 |  |  | -4 | 35 | 4.20 | 7.50 |  | 4.2 | 1.6 | 2 | 1300 | 1500
O | S72 | 70 | QA | 09 | 0005 | B | 70-QA-09-0005B | Air Handling Unit for East ITR | 2 | 2 | 0 |  | HV | Air Handling Unit | 2 x 100% | Standby | 214.4 | 16700 |  | 20040 |  |  |  | -4 | 40 |  |  | -4 | 35 | 4.20 | 7.50 |  | 4.2 | 1.6 | 2 | 1300 | 1500
O | S43 | 70 | QA | 09 | 0006 | A | 70-QA-09-0006A | Air Handling Unit for West ITR | 2 | 2 | 0 |  | HV | Air Handling Unit | 2 x 100% | Duty | 219 | 16900 |  | 20280 |  |  |  | -4 | 40 |  |  | -4 | 35 | 4.20 | 7.50 |  | 4.2 | 1.6 | 2 | 1300 | 1500 |  |  | DX type
O | S43 | 70 | QA | 09 | 0006 | B | 70-QA-09-0006B | Air Handling Unit for West ITR | 2 | 2 | 0 |  | HV | Air Handling Unit | 2 x 100% | Standby | 219 | 16900 |  | 20280 |  |  |  | -4 | 40 |  |  | -4 | 35 | 4.20 | 7.50 |  | 4.2 | 1.6 | 2 | 1300 | 1500 |  |  | DX type
O | S01 | 70 | QA | 09 | 0007 | A | 70-QA-09-0007A | Air Handling Unit for Control Building | 2 | 2 | 0 |  | HV | Air Handling Unit | 2 x 100% | Duty | 278 | 44500 |  | 53400 |  |  |  | -4 | 40 |  |  | -4 | 35 | 15.00 | 18.00 |  | 8 | 2.5 | 2.5 | 2300 | 2700
O | S01 | 70 | QA | 09 | 0007 | B | 70-QA-09-0007B | Air Handling Unit for Control Building | 2 | 2 | 0 |  | HV | Air Handling Unit | 2 x 100% | Standby | 278 | 44500 |  | 53400 |  |  |  | -4 | 40 |  |  | -4 | 35 | 15.00 | 18.00 |  | 8 | 2.5 | 2.5 | 2300 | 2700
O | S80 | 70 | QA | 09 | 0008 |  | 70-QA-09-0008 | Air Handling Unit for Admin Building | 2 | 2 | 0 |  | HV | Air handling Unit | 1 x 100% | Duty | 138 | 3400 |  | 4080 |  |  |  | -4 | 40 |  |  | -4 | 35 | 2.50 | 4.00 |  | 2.6 | 1.5 | 1.8 | 650 | 720
O | S80 | 70 | QA | 09 | 0009 | A | 70-QA-09-0009A | DX Air Handling Unit for Admin Building | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Duty | 47.3 | 6700 |  | 8040 |  |  |  | -4 | 40 |  |  | -4 | 35 | 2.20 | 4.00 |  | 2.6 | 1.2 | 1.5 | 450 | 500
O | S80 | 70 | QA | 09 | 0009 | B | 70-QA-09-0009B | DX Air Handling Unit for Admin Building | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Standby | 47.3 | 6700 |  | 8040 |  |  |  | -4 | 40 |  |  | -4 | 35 | 2.20 | 4.00 |  | 2.6 | 1.2 | 1.5 | 450 | 500
O | S80 | 70 | QA | 09 | 0010 | A | 70-QA-09-0010A | Air Handling Unit for Substation Building | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Standby | 235 | 34000 |  | 40800 |  |  |  | -4 | 40 |  |  | -4 | 35 | 20 | 23 |  | 6 | 2.5 | 2 | 3000 | 3300
O | S80 | 70 | QA | 09 | 0010 | B | 70-QA-09-0010B | Air Handling Unit for Substation Building | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Duty | 235 | 34000 |  | 40800 |  |  |  | -4 | 40 |  |  | -4 | 35 | 20 | 23 |  | 6 | 2.5 | 2 | 3000 | 3300
O | S80 | 70 | QA | 09 | 0011 | A | 70-QA-09-0011A | Air Handling Unit for Laboratory Building | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Standby | 97.6 | 3660 |  | 4392 |  |  |  | -4 | 40 |  |  | -4 | 35 | 3 | 4 |  | 2.5 | 2 | 1.2 | 900 | 1100
O | S80 | 70 | QA | 09 | 0011 | B | 70-QA-09-0011B | Air Handling Unit for Laboratory Building | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Duty | 97.6 | 3660 |  | 4392 |  |  |  | -4 | 40 |  |  | -4 | 35 | 3 | 4 |  | 2.5 | 2 | 1.2 | 900 | 1100
O | S80 | 70 | QA | 09 | 0012 | A | 70-QA-09-0012A | Air Handling Unit for Beach Valve Station | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Standby | 29 | 5238 |  | 6286 |  |  |  | -4 | 40 |  |  | -4 | 35 | 2 | 2.2 |  | 2.5 | 2 | 1.2 | 850 | 1000
O | S80 | 70 | QA | 09 | 0012 | B | 70-QA-09-0012B | Air Handling Unit for Beach Valve Station | 2 | 2 | 0 |  | HV | Air handling Unit | 2 x 100% | Duty | 29 | 5238 |  | 6286 |  |  |  | -4 | 40 |  |  | -4 | 35 | 2 | 2.2 |  | 2.5 | 2 | 1.2 | 850 | 1000
O | S80 | 70 | QU | 09 | 0001 |  | 70-QU-09-0001 | Air Cooled Condensing Unit (Warehouse building) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 50% | Duty | 1.3 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 0.50 | 0.75 |  | 0.8 | 0.4 | 0.6 | 50 | 50 | AZ-AB1-70-SK02-222004 |  | Model Daikin RXY5A-4AV1
O | S80 | 70 | QU | 09 | 0002 |  | 70-QU-09-0002 | Air Cooled Condensing Unit (Warehouse building) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 50% | Duty | 1.3 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 0.50 | 0.75 |  | 0.8 | 0.4 | 0.6 | 50 | 50 | AZ-AB1-70-SK02-222004 |  | Model Daikin RXY5A-4AV1
O | S80 | 70 | QU | 09 | 0003 |  | 70-QU-09-0003 | Air Cooled Condensing Unit for Telecom (Workshop Building) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 100% | Continuous | 3.1 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 1.16 | 1.50 |  | 0.8 | 0.4 | 0.6 | 45 | 45 | AZ-AB1-70-SK02-222003 |  | Model MSZ-AP80VGKIT Location: Plant Access Security Hut 01
O | S80 | 70 | QU | 09 | 0004 |  | 70-QU-09-0004 | Air Cooled Condensing Unit for Electrical Room (Workshop building) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 100% | Continuous | 7.8 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 2.92 | 4.00 |  | 1.1 | 0.5 | 0.85 | 90 | 90 | AZ-AB1-70-SK02-222003 |  | Plant Access Security Hut 02
O | S80 | 70 | QU | 09 | 0005 |  | 70-QU-09-0005 | Air Cooled Condensing Unit (Fire Station) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 100% | Continuous | 61.9 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 23.10 | 30.00 |  | 2.2 | 1.1 | 1.25 | 550 | 550 | AZ-AB1-70-SK02-222005 |  | Model 38ZS120
O | S89 | 70 | QU | 09 | 0006 |  | 70-QU-09-0006 | Air Cooled Condensing Unit (Main Gate House) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 100% | Continuous | 39.5 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 13.20 | 16.00 |  | 1.9 | 1 | 1.25 | 370 | 420 | AZ-AB1-70-SK02-222008 |  | Model 38ZS320
O | S89 | 70 | QU | 09 | 0007 | A | 70-QU-09-0007A | Air Cooled Condensing Unit for Beach Valve Station | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Duty | 29 | [6 empty] | -4 | 40
O | S89 | 70 | QU | 09 | 0007 | B | 70-QU-09-0007B | Air Cooled Condensing Unit for Beach Valve Station | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Standby | 29 | [6 empty] | -4 | 40
O | S80 | 70 | QU | 09 | 0008 |  | 70-QU-09-0008 | Air Cooled Condensing Unit for Security Hut 02 (Office) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 100% | Continuous | 1.3 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 0.50 | 0.75 |  | 0.6 | 0.35 | 0.5 | 28 | 32 | AZ-AB1-70-SK02-222009
O | S80 | 70 | QU | 09 | 0009 |  | 70-QU-09-0009 | Air Cooled Condensing Unit for Security Hut 02 (Security Cabin) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 100% | Continuous | 2.4 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 0.90 | 1.10 |  | 0.7 | 0.4 | 0.6 | 34 | 38 | AZ-AB1-70-SK02-222009
O | S80 | 70 | QU | 09 | 0010 |  | 70-QU-09-0010 | Air Cooled Condensing Unit for Security Hut 01 | 2 | 2 | 0 |  | HV | Air Cooling Unit | 1 x 100% | Continuous | 2.5
O | S72 | 70 | QU | 09 | 0011 | A | 70-QU-09-0011A | Air Cooled Condensing Unit ITR East Utilities | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Duty | 214.4 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 75.00 | 90.00 |  | 4.5 | 1.3 | 2.2 | 1700 | 1900 | AZ-AB1-70-SK02-222011 |  | Model 38ZS320
O | S72 | 70 | QU | 09 | 0011 | B | 70-QU-09-0011B | Air Cooled Condensing Unit ITR East Utilities | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Standby | 214.4 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 75.00 | 90.00 |  | 4.5 | 1.3 | 2.2 | 1700 | 1900 | AZ-AB1-70-SK02-222011 |  | Model MSZ-AP80VGKIT
O | S43 | 70 | QU | 09 | 0012 | A | 70-QU-09-0012A | Air Cooled Condensing Unit ITR West Process | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Duty | 219.0 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 75.00 | 90.00 |  | 4.5 | 1.3 | 2.2 | 1700 | 1900 | AZ-AB1-70-SK02-222010
O | S43 | 70 | QU | 09 | 0012 | B | 70-QU-09-0012B | Air Cooled Condensing Unit ITR West Process | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Standby | 219.0 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 75.00 | 90.00 |  | 4.5 | 1.3 | 2.2 | 1700 | 1900 | AZ-AB1-70-SK02-222010
O | S80 | 70 | QU | 09 | 0013 | A | 70-QU-09-0013A | Air Cooled Condensing Unit (Admin Bldg) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Duty | 219.0 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 15.00 | 18.00 |  | 2.3 | 1.1 | 1.6 | 400 | 440 | AZ-AB1-70-SK02-222006
O | S80 | 70 | QU | 09 | 0013 | B | 70-QU-09-0013B | Air Cooled Condensing Unit (Admin Bldg) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Standby | 219.0 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 15.00 | 18.00 |  | 2.3 | 1.1 | 1.6 | 400 | 440 | AZ-AB1-70-SK02-222006
O | S80 | 70 | QU | 09 | 0014 | A | 70-QU-09-0014A | Air Cooled Condensing Unit (Laboratory Bldg) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Duty | 97.6 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 30 | 35 |  | 3 | 1.2 | 1.8 | 800 | 1000
O | S80 | 70 | QU | 09 | 0014 | B | 70-QU-09-0014B | Air Cooled Condensing Unit (Laboratory Bldg) | 2 | 2 | 0 |  | HV | Air Cooling Unit | 2 x 100% | Standby | 97.6 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 30 | 35 |  | 3 | 1.2 | 1.8 | 800 | 1000 |  |  | Model MSZ-AP80VGKIT
O | S80 | 70 | UE | 09 | 0001 |  | 70-UE-09-0001 | Chilling Water Unit (Warehouse building) | 2 | 2 | 0 |  | HV | Air Cooled Chiller | 1 x 100% | Continuous | 96.3 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 32.10 | 40.00 |  | 2.6 | 1.2 | 2 | 1100 | 1250 |  |  | Model Carrier 30RB160
O | S80 | 70 | UE | 09 | 0002 |  | 70-UE-09-0002 | Chilling Water Unit for Workshop Building | 2 | 2 | 0 |  | HV | Air Cooled Chiller | 1 x 100% | Continuous | 509.5 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 190.00 | 220.00 |  | 4.8 | 2.25 | 2.3 | 3737 | 4036 |  |  | Model Carrier 30XBEZE-350
O | S01 | 70 | UE | 09 | 0003 | A | 70-UE-09-0003A | Chilling Water Unit for Control Building | 2 | 2 | 0 |  | HV | Air Cooled Chiller | 2 x 100% | Duty | 61.9 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 95.00 | 110.00 |  | 4.5 | 2.3 | 2.6 | 2400 | 2600 |  |  | Model 30RB160
O | S01 | 70 | UE | 09 | 0003 | B | 70-UE-09-0003B | Chilling Water Unit for Control Building | 2 | 2 | 0 |  | HV | Air Cooled Chiller | 2 x 100% | Standby | 61.9 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 95.00 | 110.00 |  | 4.5 | 2.3 | 2.6 | 2400 | 2600 |  |  | Model 30RB160
O | S80 | 70 | UE | 09 | 0004 |  | 70-UE-09-0004 | Chilling Water Unit for Admin Building | 2 | 2 | 0 |  | HV | Air Cooled Chiller | 1 x 100% | Continuous | 138 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 52.00 | 75.00 |  | 3.8 | 1.5 | 2.3 | 1600 | 1850 |  |  | Model 30XBEZE-400
O | S80 | 70 | UE | 09 | 0005 | A | 70-UE-09-0005A | Chilling Water Unit for Admin Building | 2 | 2 | 0 |  | HV | Air Cooled Chiller | 2 x 100% | Duty | 240 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 80 | 90 |  | 3.5 | 2.25 | 2.32 | 2000 | 2100 |  |  | Model 30XBEZE-900
O | S80 | 70 | UE | 09 | 0005 | B | 70-UE-09-0005B | Chilling Water Unit for Admin Building | 2 | 2 | 0 |  | HV | Air Cooled Chiller | 2 x 100% | Standby | 240 | [6 empty] | -4 | 40 |  |  | -4 | 35 | 80 | 90 |  | 3.5 | 2.25 | 2.32 | 2000 | 2100 |  |  | Model 30XBEZE-900
O | S80 | 70 | UP | 09 | 0001 |  | 70-UP-09-0001 | Humidifier (Warehouse building) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 30 | 18119 |  | 34.06 | [9 empty] | 28 | 30 |  | 0.8 | 0.7 | 1.6 | 120 | 140
O | S80 | 70 | UP | 09 | 0002 |  | 70-UP-09-0002 | Humidifier (Main Gate House) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 15 | 6500 |  | 16.73 | [9 empty] | 14 | 15 |  | 0.7 | 0.6 | 1.5 | 100 | 120 | AZ-AB1-70-SK02-222008
O | S80 | 70 | UP | 09 | 0003 |  | 70-UP-09-0003 | Humidifier (Fire Station) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 25 | 5600 |  | 26.64 | [9 empty] | 22 | 25 |  | 0.6 | 0.5 | 1.4 | 85 | 100
O | S01 | 70 | UP | 09 | 0004 |  | 70-UP-09-0004 | Humidifier for HVAC Room (Control Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent |  | 44500 |  | 145.1 | [9 empty] | 120 | 140 |  | 1 | 1 | 2 | 400 | 550
O | S89 | 70 | UP | 09 | 0005 |  | 70-UP-09-0005 | Humidifier (Substation Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 110 | 34000 |  | 128 |  |  |  | -4 | 40 |  |  | -4 | 35 | 90 | 110 |  | 0.8 | 1 | 1.5 | 350 | 400
O | S01 | 70 | UP | 09 | 0006 |  | 70-UP-09-0006 | Humidifier (Workshop Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 110 | 34000 |  | 128 |  |  |  | -4 | 40 |  |  | -4 | 35 | 90 | 110 |  | 0.8 | 1 | 1.5 | 350 | 400
O | S01 | 70 | UP | 09 | 0007 |  | 70-UP-09-0007 | Humidifier (Admin Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 510 | 24000 |  | 78 |  |  |  | -4 | 40 |  |  | -4 | 35 | 55 | 65 |  | 0.5 | 0.6 | 1.1 | 80 | 115
O | S01 | 70 | UP | 09 | 0008 |  | 70-UP-09-0008 | Humidifier (Admin Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 83 | 3400 |  | 23 |  |  |  | -4 | 40 |  |  | -4 | 35 | 16 | 18 |  | 0.4 | 0.5 | 0.9 | 45 | 55
O | S01 | 70 | UP | 09 | 0009 |  | 70-UP-09-0009 | Humidifier (ITR East Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 47 | 6700 |  | 5 |  |  |  | -4 | 40 |  |  | -4 | 35 | 3.5 | 4 |  | 0.3 | 0.4 | 0.5 | 20 | 25
O | S01 | 70 | UP | 09 | 0010 |  | 70-UP-09-0010 | Humidifier (ITR West Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 219 | 17000 |  | 28 |  |  |  | -4 | 40 |  |  | -4 | 35 | 19 | 22 |  | 0.4 | 0.6 | 1 | 60 | 80
O | S01 | 70 | UP | 09 | 0011 |  | 70-UP-09-0011 | Humidifier (Laboratory Bldg) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 219 | 17000 |  | 28 |  |  |  | -4 | 40 |  |  | -4 | 35 | 19 | 22 |  | 0.4 | 0.6 | 1 | 60 | 80
O | S01 | 70 | UP | 09 | 0012 |  | 70-UP-09-0012 | Humidifier (Beach valve station) | 2 | 2 | 0 |  | HV | Steam Generator | 1 x 100% | Intermittent | 97.6 | 3660 |  | 16.87 |  |  |  | -4 | 40 |  |  | -4 | 35 | 11 | 13 |  | 0.5 | 0.4 | 0.8 | 50 | 60
O |  | 70 | JB | 78 | 0001 |  | 70-JB-78-0001 | Mobile Crane (30 Tonne) | 1 | 1 |  |  | ME | Crane |  |  | 29 | 5238 |  | 1 |  |  |  | -4 | 40 |  |  | -4 | 35 | 1 | 1.2 |  | 0.3 | 0.3 | 0.5 | 30 | 35 |  |  | Required for Mechanical Handling
O |  | 70 | JB | 78 | 0002 |  | 70-JB-78-0002 | Mobile Crane (60 Tonne) | 1 | 1 |  |  | ME | Crane | [25 empty] | Required for Mechanical Handling - likely to be the optimised crane solution - to be confirmed during detailed engineering.
O |  | 70 | JB | 78 | 0003 |  | 70-JB-78-0003 | Mobile Crane (100 Tonne) | 1 | 1 |  |  | ME | Crane | [25 empty] | Required for Mechanical Handling
O |  | 70 | JC | 78 | 0001 |  | 70-JC-78-0001 | Overhead Crane - Export Compressor Shelter ( 15 Te SWL) | 1 | 1 |  |  | ME | Crane |  |  | TBA | [22 empty] | Required for Mechanical Handling
O |  | 70 | JC | 78 | 0002 |  | 70-JC-78-0002 | Overhead Crane - Flash Gas Compressor Shelter ( 10 Te SWL) | 1 | 1 |  |  | ME | Crane |  |  | TBA | [22 empty] | Required for Mechanical Handling
O |  | 70 | JC | 78 | 0003 |  | 70-JC-78-0003 | Overhead Crane - Workshop Building (10 Te SWL) | 1 | 1 |  |  | ME | Crane |  |  | TBA | [22 empty] | Required for Mechanical Handling
O |  | 70 | JD | 78 | 0001 |  | 70-JD-78-0001 | Lifting Davit - PSV Platform (500 kg SWL) | 1 | 1 |  |  | ME | Crane | [25 empty] | Required for Mechanical Handling - for secondary lifting from PSV and fin fan level
O |  | 70 | JD | 78 | 0002 |  | 70-JD-78-0002 | Lifting Davit - Export Compressor After Cooler (500 kg SWL) | 1 | 1 |  |  | ME | Crane | [25 empty] | Required for Mechanical Handling - for secondary lifting from PSV and fin fan level
O |  | 70 | JD | 78 | 0003 |  | 70-JD-78-0003 | Lifting Davit - 2nd Stage Suction Cooler Platform (500 kg SWL) | 1 | 1 |  |  | ME | Crane | [25 empty] | Required for Mechanical Handling - for secondary lifting from PSV and fin fan level
O |  | 70 | JD | 78 | 0004 |  | 70-JD-78-0004 | Lifting Davit - Heating Medium Dump Cooler (500 kg SWL) | 1 | 1 |  |  | ME | Crane | [25 empty] | Required for Mechanical Handling - for secondary lifting from PSV and fin fan level
O |  | 70 | JD | 78 | 0005 |  | 70-JD-78-0005 | Compressor Bundle Extractor | 1 | 1 |  |  | ME | Crane |  |  | TBA | [22 empty] | Required for Mechanical Handling - Supplied by the equipment VENDOR
O |  | 70 | JD | 78 | 0006 |  | 70-JD-78-0006 | Compressor Motor Rotor Extractor | 1 | 1 |  |  | ME | Crane |  |  | TBA | [22 empty] | Required for Mechanical Handling - Supplied by the equipment VENDOR
O |  | 70 | JD | 78 | 0007 |  | 70-JD-78-0007 | Shell and Tube Bundle Extractor (20 Te SWL) | 1 | 1 |  |  | ME | Crane |  |  | TBA | [22 empty] | Required for Mechanical Handling - Supplied by the equipment VENDOR
O |  | 70 | JD | 78 | 0008 |  | 70-JD-78-0008 | Portable Lifting Gantry / A-Frame (1 Te SWL) | 1 | 1 |  |  | ME | Crane | [25 empty] | Required for Mechanical Handling
O |  | 70 | JH | 78 | 0001 |  | 70-JH-78-0001 | Power Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JH | 78 | 0002 |  | 70-JH-78-0002 | Power Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist |  |  | TBA | [22 empty] | Required for Mechanical Handling
O |  | 70 | JH | 78 | 0003 |  | 70-JH-78-0003 | Power Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist |  |  | TBA | [22 empty] | Required for Mechanical Handling
O |  | 70 | JH | 78 | 0004 |  | 70-JH-78-0004 | Power Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist |  |  | TBA | [22 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0001 |  | 70-JTS-78-0001 | Manual Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0002 |  | 70-JTS-78-0002 | Manual Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0003 |  | 70-JTS-78-0003 | Manual Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0004 |  | 70-JTS-78-0004 | Manual Hoists (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0005 |  | 70-JTS-78-0005 | Puller (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0006 |  | 70-JTS-78-0006 | Puller (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0007 |  | 70-JTS-78-0007 | Puller (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JTS | 78 | 0008 |  | 70-JTS-78-0008 | Puller (various capacities) | 1 | 1 |  |  | ME | Chain Hoist | [25 empty] | Required for Mechanical Handling
O |  | 70 | JY | 78 | 0001 |  | 70-JY-78-0001 | Telehandler (3.5 Te SWL) | 1 | 1 |  |  | ME | Forklift | [25 empty] | Required for Mechanical Handling
O |  | 70 | JY | 78 | 0002 |  | 70-JY-78-0002 | Forklift (5.5Te SWL) | 1 | 1 |  |  | ME | Forklift | [25 empty] | Required for Mechanical Handling
O |  | 70 | JY | 78 | 0003 |  | 70-JY-78-0003 | Scissor Lift (500kg SWL) | 1 | 1 |  |  | ME | Forklift | [25 empty] | Required for Mechanical Handling - Manual push pull Scissor lift with hydraulic power lifting table SWL 500kg for all air cooler motors
O |  | 70 | JY | 78 | 0004 |  | 70-JY-78-0004 | Tow Trolley (1 Te SWL) | 1 | 1 |  |  | ME | Forklift | [25 empty] | Required for Mechanical Handling

## Sheet4
SWGR/MCC No. | Bus | SWGR/MCC No. & Bus | Equipment Tag No. | EQUIPMENT Description | Type of Service N-Normal, Em-Emergency, SA-UPS Power | Load Type | Voltage [KV] | Starter Type | Load Duty | Absorbed Power (kW) [A] | Rated Power (kW) [B] | Full Load Current
70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1003 Main Motor | Export Compressor _ Main Motor | N | VSD-HV | 11 |  | C | 7109 | 8000 | 384.6657
70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-KA-31-2003 Main Motor | Export Compressor _ Main Motor | N | VSD-HV | 11 |  | C | 7109 | 8000 | 384.6657
70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0001A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11 |  | C |  | 853.7374
70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0001B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgeard B | N | F | 11 |  | C |  | 160.7903
70-IJ-61-0001 |  | 70-IJ-61-0001C | 70-IV-61-0001C | 11/0.72kV Transformer Feeder C for 690V Emergency Switchgear C | Em | F | 11 |  | C |  | 1473.6042
70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0003A | 11/0.72kV Transformer Feeder A for 690V Normal Process Switchgear A | N | F | 11 |  | C |  | 1025.4943
70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0003B | 11/0.72kV Transformer Feeder B for 690V Normal Process Switchgear B | N | F | 11 |  | C |  | 791.0112
70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-IV-61-0002A | 11/0.42kV Transformer Feeder A for 400V Normal Switchgear A | N | F | 11 |  | C |  | 596.0706
70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-IV-61-0002B | 11/0.42kV Transformer Feeder B for 400V Normal Switchgear B | N | F | 11 |  | C |  | 501.7079
70-IJ-61-0001 | B | 70-IJ-61-0001C | 81-IV-61-0001 | 11/0.42kV Transformer Feeder for Beach Valve Substation LV Transformer | N | F | 11 |  | C | 100 | 100 | 5.411
70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-A-20-0002A -Main Motor | Condensate Recycle Booster Pump A | N | M-HV | 11 |  | I | 539 | 600 | 33.2825
70-IJ-61-0001 | B | 70-IJ-61-0001B | 70-A-20-0002B -Main Motor | Condensate Recycle Booster Pump B | N | M-HV | 11 |  | S | 539 | 600 | 33.2825
70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-KA-31-1001/1002-Main Motor | Main Motor for Flash Gas Compressor | N | M-HV | 11 |  | C | 1044 | 1500 | 64.4656
70-IJ-61-0001 | B | 70-IJ-61-0001C | 70-PA-01-0002 Panel(Main Motor Power) | Electric Firewater Pump UCP | N | M-HV | 11 | SS | I | 375 | 600 | 23.1558
70-IJ-61-0001 | A | 70-IJ-61-0001A | 70-UZ-43-0002 | MEG Regeneration Package - Electic Reboiler | N | F | 11 |  | C | 3000 | 3000 | 157.4592

## Sheet6
(Breaker Type = VCB, 11 kV class; Rating = continuous current In)
No. | Equipment Tag No. | Breaker Type | Rating (A)
1 | 70‑KA‑31‑1003 | VCB 11 kV | 1250
2 | 70‑KA‑31‑2003 | VCB 11 kV | 1250
3 | 70‑A‑20‑0002A | VCB 11 kV | 630
4 | 70‑A‑20‑0002B | VCB 11 kV | 630
5 | 70‑KA‑31‑1001/1002‑Main | VCB 11 kV | 630
6 | 70‑PA‑01‑0002 | VCB 11 kV | 630
7 | 70‑UZ‑43‑0002 | VCB 11 kV | 630
8 | 70‑UZ‑43‑0002‑SP | VCB 11 kV | 630
9 | 70‑HE‑35‑0001‑TR | VCB 11 kV | 630
10 | 70‑IV‑61‑0001A | VCB 11 kV | 630
11 | 70‑IV‑61‑0001B | VCB 11 kV | 630
12 | 70‑IV‑61‑0003A | VCB 11 kV | 630
13 | 70‑IV‑61‑0003B | VCB 11 kV | 630
14 | 70‑IV‑61‑0002A | VCB 11 kV | 630
15 | 70‑IV‑61‑0002B | VCB 11 kV | 630
Notes (basis you can keep with the sheet)
* Selection rule used: choose breaker In ≥ design current (≈1.25×FLC) and round up to the next standard rating; this follows IEC selection practice for protective devices (Ib ≤ In, coordination with cable/installation).
* Standard 11 kV VCB continuous ratings commonly available: 630, 800, 1250, 1600, 2000, 2500, 3150 A; hence most feeders land on 630 A, and large motors on 1250 A.